## 1. Read Me
Solar Mini Grid (SMG) Initial System Planning Tool |  |  | सौर्य मिनी ग्रिड (एसएमजी) प्राथमिक प्रणाली योजना
Version: |  | 1.0
Developer: |  | Ajay Thapa
About | 1 | This design workbook serves as a basic sizing tool to estimate the key SMG component sizes and system costs. It shall not be used for detail design and costing. | 1 | यो डिजाइन वर्कबुकले मुख्यतया सौर्य मिनिग्रिडको आकार र प्रणाली लागतको अनुमान गर्ने आधारभुत कार्य गर्दछ। यसलाई विस्तृत डिजाइन र लागतमा प्रयोग गर्नुहुदैन ।
| 2 | The designer (or the user) shall only have to enter project data in the 'Inputs' sheet. All other sheets are interlinked and a report is generated in the 'Report' sheet. The designer may update the pricing in the 'Price reference 1' sheet. | 2 | निर्माताले (वा प्रयोगकर्ताले) 'इनपुट'(Input) पानामा मात्र परियोजना डाटा प्रविष्ट गर्नुपर्नेछ। अन्य सबै पानाहरू एकसाथ जडित छन् र 'रिपोर्ट' पानामा रिपोर्ट तयार हुन्छ। निर्माताले 'मूल्य संदर्भ ' (Reference Prices) पानामा मूल्य अद्यावधिक गर्न सक्नुहुनेछ।
| 3 | The designer may select the Balance of Systems of their choice with simple Yes/No function in the 'Inputs' sheet. This will result in inclusion or exclusion of the component in the BoQ. | 3 | डिजाइनरले 'Input' पानामा आवश्यक छ/ आवश्यक छैन प्रकार्यको साथ प्रणालीहरुको चयन गर्न सक्नु हुनेछ । यसले BoQ मा कम्पोनेन्ट समावेस वा बहिस्कारको परिणाम दिनेछ ।
| 4 | The rates used in the SMG tool are taken as reference from AEPC implemented projects.The designer should change the rate of equipments as per the district rates or Quotations received from the installer companies to prepare the BoQ. | 4 | यस tools मा प्रयोग भएका दररेटहरु बैकल्पिक उर्जा प्रबर्धन केन्द्रबाट कार्यान्वयन भएका योजनाहरु बाट साभार गरिएको हो।तर डिजाइनरले BoQ तयार गर्दा प्रचलित जिल्ला दररेटहरु वा जडान कम्पनीहरुबाट Quotation लिई उपकरणहरुको प्रति एकाइ दररेट राख्नुपर्छ।
| 5 | The length of the cable when it is unknown can be calculate with two methods: "The method by connection" and "The method by capacity". The choice of the method can be choose in the Design sheet. | 5 | केबलको लम्बाइ थाहा नभएको अवस्थामा दुईवटा विधिहरूद्वारा गणना गर्न सकिन्छ: "जडानद्वारा विधि" र "क्षमताद्वारा विधि"। विधिको छनोट ब्याकइन्ड डिजाइन (Backend Design) पानामा छनौट गर्न सकिन्छ।
Limitations | 1 | The design can not be used for detailed feasibility study of the projects. | 1 | यो डिजाइन tool कुनै पनि सौर्य मिनी-ग्रिड आयोजनाको विस्तृत सम्भाव्यता अध्ययनका लागि प्रयोग गर्न सकिँदैन।
| 2 | The cost of the materials have been included for reference purpose only and not as per the current district rate. The pricelist section must be updated every year and a separate window to enter the pricelist of indicated items must be there in the web design | 2 | सामग्रीको मूल्य हालको जिल्ला दररेट अनुसार Reference प्रयोजनको लागि मात्र समावेस गरिएको छ। Reference Prices खण्ड प्रत्येक वर्ष अद्यावधिक गरिनुपर्छ।
| 3 | The design consist of only the electrical part of the solar mini-grid, the civil components like powerhouse construction, mounting poles, etc are not considered. | 3 | यो डिजाइनले सोलर मिनी-ग्रिडको केवल विद्युतीय अंशलाई मात्र समावेश गर्दछ, विद्युतगृह निर्माण, माउन्टिङ पोल आदि जस्ता सिभिल कम्पोनेन्टहरू समावेश गरिएको छैन।
| 4 | The size of the inverters above 25kW will have inverters size with respect to closest value of multiples of 25kW size inverter only. | 4 | २५ कि. वा. भन्दा माथिको इन्भर्टरको साईज़मा २५ कि. वा. साईज़को इन्भर्टरको गुणकको निकटतम मानको सन्दर्भमा इन्भर्टरको साईज़ हुनेछ।
| 5 | The transporation cost for the goods are not considered, the transporation cost may vary as per the geographic location where there may be use of air-lifting. Also, the cost of services is not included in the BoQ sheet. | 5 | यस tool मा मालसामानको ढुवानी लागत र सेवाहरूको लागत समावेस गरिएको छैन । भौगोलिक स्थान अनुसार हवाई ढुवानी प्रयोग हुन सक्ने भएकोले लागत फरक हुन सक्छ।
Assumptions | 1 | The peak sun hours used for the system design is 4.5 kWh/m2 per day; Losses calculated as 30% | 1 | प्रणालीको डिजाइनका लागि प्रयोग गरिएको उच्चतम सूर्यको घण्टा 4.5 kWh/m2 प्रतिदिन लिईएको छ। घाटा 30% को रुपमा गणना गरिएको छ।
| 2 | Minor Components like nut bolts, cable ties, washers, glands, tapes, conduits etc. are taken in Lump sum | 2 | साना सामाग्रीहरु जस्तै नट बोल्ट, केबल टाई, वाशर, ग्रन्थी, टेप, कन्ड्युट्स आदि एकमुष्टमा लिईएको छ ।
| 3 | A contingency of 10% is added before VAT to the total system cost. | 3 | कुल प्रणाली लागतमा मूल्य अभिवृद्धि करअघि १०% को आकस्मिकता थपिएको छ।
| 4 | This design consider only single faced PV modules only. | 4 | यो डिजाइनले एकल फेस गरिएको PV मोड्युललाई मात्र विचार गर्छ ।
Site Selection Parameters | 1 | Availability of Solar Resource: 1. Global Horizontal Irradiance (GHI) with more than 4.5 kWh/m^2 shoule be considered to have higher energy yield. 2. GHI value should be validated from freely available or commercially available meteorological data sources for different chosen sites | 1 | सौर्य स्रोतको उपलब्धता: 1. 4.5 kWh/m2 भन्दा बढी भएको ग्लोबल होरिजन्टल विकिरण (GHI) लाई उच्च ऊर्जा उपज भएको मानिन्छ। 2. GHI मान स्वतन्त्र रूपमा उपलब्ध वा व्यावसायिक रूपमा उपलब्ध मौसमी आँकडा स्रोतहरूबाट मान्यतापूर्वक प्रमाणित गर्नुपर्छ।
| 2 | Shading: 1. Far Shading: Shading due to hills or mountains or building on the far horizon should be avoided. 2. Near Shading: Shading due to nearby trees, building, structures, overhead cabling should be avoided. | 2 | छायांकन 1. दूरीबाट आएको छायांकन: दूरीबाट आएका पहाड, हिमाल, वा टाढा क्षितिजमा भवनको कारण छाया हुनबाट जोगिनु पर्छ। 2. नजिकबाट आएको छायांकन: नजिकैको रुख, भवन, संरचना, ओभरहेड केबलिङको कारणले छायाँ लगाउनु हुँदैन।
| 3 | Availability of Land Area: 1. Should have sufficient space to accommodate the required capacity to be installed. 2. Typically require about 7 to 10 m2 per kWp for relatively flat land and depends on two factors: a. Type of solar PV technology chosen (PolyCrystalline or MonoCrystalline or HIT or Thin Film). b. Land Shape and slope, tilt angle and shading. | 3 | जग्गाको उपलब्धता: 1. आवश्यक क्षमताको प्रणाली जडान गर्नलाई पर्याप्त जग्गा उपलब्ध हुनुपर्छ। 2. साधारणतया समतल जग्गाका लागि प्रति किलोवाट पिक (kWp) लाग्ने लगभग 7 देखि 10 वर्गमीटरको क्षेत्र आवश्यक हुन्छ र यसले दुई कारकमा निर्भर गर्दछ: a.सौर्य PV प्रविधिको प्रकार (PolyCrystalline वा MonoCrystalline वा HIT वा Thin film). b.जग्गाको आकार, झुकावको कोण, टिल्ट कोण र छायांकन
| 4 | Topography and Orientation: 1.Land should have a good southern exposure without significant shading. 2.Sites that are flat or slope towards the south are ideal. | 4 | भूगोल र दिशा: 1. जग्गा महत्त्वपूर्ण छाया बिना दक्षिणी मोहोडा फर्केको हुनुपर्दछ 2. दक्षिणतिर समतल वा ढल्किएको स्थानहरू उपयुक्त हुन्छन ।
| 5 | Accessibility: 1. Shortest possible distance should be chosen from project site to access road and highway. 2. Quality of existing roads or new proposed construction roads should be carefully considered for the transportation of equipment (by vehicle or by porter). 3. There should not be the access of grid electricity for at least three years for the installation of solar mini-grid project. | 5 | पहुँच: 1. आयोजना स्थलबाट सडक र राजमार्गमा पुग्नको लागि सबैभन्दा छोटो दूरी छनोट गर्नुपर्छ। 2. उपकरणको ढुवानी (गाडी वा भरिया द्वारा) को लागि अवस्थित सडक वा नयाँ प्रस्तावित सडकहरूको गुणस्तर सावधानीपूर्वक विचार गर्नुपर्छ। 3.सोलार मिनी ग्रिड आयोजना स्थापनाका लागि कम्तिमा तीन वर्षसम्म राष्ट्रिय प्रसारण विद्युतको पहुँच नहुने स्थान हुनु पर्नेछ।
| 6 | Climatic Characterstics: 1. Flooding: Flood risk assessment mainly to the powerhouse, erosion of mounting structure and foundations. 2. Wind Speed: Sites with high wind speed should be avoided. 3. Snow: a. Sites prone to regular covering of snow areas should be avoided. b. For low snow areas, the design of array mounting structures should consider the extra weight of snow. 4. Landslide: The area prone to landslide mainly to the powerhouse, mounting structure should be ignored. | 6 | जलवायुगत विशेषताहरू: 1. बाढी: बाढी जोखिम मूल्याङ्कन मुख्यतया पावरहाउस, माउन्टिंग संरचना र जगको क्षरण। 2. हावाको गति: उच्च हावाको गति भएका स्थलहरूलाई बेवास्ता गर्नुपर्छ। 3. हिउँ: a. नियमित रूपमा हिउँले ढाकिएको क्षेत्रहरूलाई बेवास्ता गर्नुपर्छ। b. हिउँपर्ने क्षेत्रहरूका लागि, Array माउन्टिंग संरचनाको डिजाइनले हिउँको अतिरिक्त वजनलाई महत्व दिनुपर्छ। 4. सोलार Array लोकेसन र पावर हाउस क्षेत्रहरू लाई पहिरो प्रवण क्षेत्रहरू चयन गर्न बाट जोगाउनु पर्छ।
Legend | 1 | Inputs to be provided by the user | 1 | प्रयोगकर्ताद्वारा प्रदान गरिने इनपुटहरू
| 2 | Dropdown options | 2 | ड्रपडाउन विकल्पहरू
| 3 | Recommended default values. Subject to modification, if required. However, alteration require expert knowlede. | 3 | प्रस्तावित पूर्वनिर्धारित मूल्यहरू। आवश्यक भएमा परिमार्जन गर्न सकिन्छ। तथापि, परिमार्जन गर्नका लागि विशेषज्ञ ज्ञान आवश्यक छ।
| 4 | Linked cells | 4 | लिङ्क गरिएका cells
This tool was produced with funding from the Federal Ministry for Economic Cooperation and Development (BMZ), Germany through Deutsche Gesellschaft für Internationale Zusammenarbeit (GIZ) GmbH.
Published by
The Government of Nepal
Ministry of Energy, Water Resources and Irrigation
Alternative Energy Promotion Centre (AEPC)
Mid Baneshwor, Post Box No.: 14364, Kathmandu, Nepal Tel: +977-1-4498013/4498014
Email: info@aepc.gov.np
Web: www.aepc.gov.np
With support of
Deutsche Gesellschaft für Internationale Zusammenarbeit (GIZ) GmbH
Promotion of Solar Technologies for Economic Development (POSTED) NTNC Complex, Khumaltar, Lalitpur, Nepal
P.O. Box 1457, Kathmandu, Nepal
Tel: +977 1 5555 289, 5538 129
Email: posted@giz.de
Developed by
Integration Umwelt & Energie GmbH, Germany
Author: Ajay Thapa
Review: Kushal Gautam, Muhammed Imran, Nipun Regmi
Layout: Muhammed Imran
April 2024
Password
AEPC-POSTED-SMG-AT

## 2. Inputs
Inputs |  |  |  | इनपुटहरू
| Benificiary Information |  |  | प्रयोगकर्ताको जानकारी
| Name of User Committee/Cooperative/ Local Government | Miklajung SMG |  | उपभोक्ता समिति/सहकारी/स्थानीय सरकारको पुरा नाम
| No. Beneficiaries Households | 100 |  | लाभान्वितहरुको घरधुरी संख्या
| No. of Enterprises | 21 |  | हालको अवस्थित उद्यम संख्या + थपिने उद्यमहरूको संख्या
| Name of Chairperson | Rajesh Magar |  | अध्यक्षको नाम र थर
| Mobile No. | 9812341234 |  | मोबाइल नम्बर (कृपया १० अक्षरको आफ्नो मोबाईल नम्बर राख्नुहोस)
| Province | Koshi Province |  | प्रदेश
| District | Panchthar |  | जिल्ला
| R/Municipality | Sewaroo RM |  | गाउँपालिका/नगरपालिका
| Ward no. | 10 |  | वार्ड नं
| Tole name | Chilime |  | टोलको नाम
| Designer Information |  |  | डिजाइनरको विवरण
| Name of Designer | Robert Mugabe |  | डिजाइन गर्ने व्यक्तिको पूरा नाम
| Designation | Engineer |  | डिजाइन गर्ने व्यक्तिको पद
| Organization | RM1as |  | कार्यालयको नाम
| Date | 2024-04-12 |  | मिति
| Design Inputs |  |  | डिजाइन इनपुटहरू
| Proximity to nearest Three Phase NEA Grid (Km) | 100 |  | राष्ट्रिय प्रसारण लाईनको निकटता
| NEA grid supply phase | Three Phase |  | राष्ट्रिय प्रसारण लाईनको आपूर्ति फेज
| NEA grid supply voltage | 400 |  | राष्ट्रिय प्रसारण लाईनको आपूर्ति भोल्टेज
| Distance between PV Array and Proposed Powerhouse location(m) | 100 |  | सौर्य पाता र प्रस्तावित पावरहाउस स्थान बीचको दूरी (मि)
| Power house to first pole (m) | 25 |  | पावरहाउस देखि पहिलो पोलसम्मको दुरी (मी)
| Length for the Transmission and Distribution | Unknown |  | प्रसारण र वितरणको लम्बाइ (मी)
| Known length for the Transmission and Distribution (m) | 5000 |  | प्रसारण र वितरणको लम्बाइ (मि)
| Estimated length for the Transmission and Distribution (m) | 11715.6827 |  | प्रसारण र वितरणको लागि अनुमानित लम्बाइ (मी) | [7 empty] | -
| Do you know the total power demand and energy demand ? | NO |  | के तपाईलाई कुल बिजुलीको माग र उर्जाको माग थाहा छ?
| Total power demand (kW) | 150 |  | कुल विद्युत माग (kW)
| Total energy demand (kWh) | 600 |  | कुल ऊर्जा माग (kWh)
The below tables are only to be filled if the answer to is D31 is "No" |  |  |  | यदि सेल नम्बर D31 को उत्तर "No" हो भने मात्र तलको तालिका भर्नुहोला
Household Demand
| Household Equipments | No. | Watt | Total watts | Hours | Watt hour
| Enter No. of Bulbs Required | 5 | 10 | 50 | 1 | 50
| Television | 1 | 80 | 80 | 1 | 80
| Mobile Charger | 1 | 5 | 5 | 1 | 5
| Radio | 1 | 5 | 5 | 1 | 5
| Dish Home | 1 | 40 | 40 | 1 | 40
| Desktop Computer | 1 | 120 | 120 | 1 | 120
|  | Total W/Hh |  | 300 | Total kWh | 0.3
| Total Number of Households in the community |  |  |  |  | 100
| Total Household Demand |  |  | 30 | kW | 30 | kWh
Productive Energy Use Load Demand
| Productive Equipments | No. | Watt | Total watts | Hours | Watt hour
| Agro Processing Mills | 0 | 1500 | 0 | 0 | 0
| Saw Mills | 3 | 2000 | 6000 | 3 | 18000
| Mobile Shops | 5 | 200 | 1000 | 2 | 2000
| Tailoring Business | 10 | 1000 | 10000 | 1 | 10000
| Grill Udhyog | 1 | 1500 | 1500 | 1 | 1500
| Private Clinic | 2 | 320 | 640 | 3 | 1920
| Bakery Udhyog | 0 | 0 | 0 | 0 | 0
| Poultary Farm | 0 | 0 | 0 | 0 | 0
| Total PEU kWh |  |  | 19.14 | kW | 33.42 | kWh
Public Energy Use Load Demand
| Productive Equipments | No. | Watt | Total watts | Hours | Watt hour
| Healthpost | 2 | 1200 | 2400 | 12 | 28800
| Schools | 1 | 4.09 | 4.09 | 6 | 24.54
| Street Lights | 30 | 20 | 600 | 12 | 7200
| Total number of government offices | 5 | 550 | 2750 | 8 | 22000
| Temples | 7 | 100 | 700 | 5 | 3500
| Community Building | 1 | 300 | 300 | 5 | 1500
| Total PEU kWh |  |  | 5.7541 | kW | 63.0245 | kWh
| Total Daily Load |  |  | 54.8941 | kW | 126.4445 | kWh
| Usage timetable – Use only if required | 0-1 | 1-2 | 2-3 | 3-4 | 4-5 | 5-6 | 6-7 | 7-8 | 8-9 | 9-10 | 10-11 | 11-12 | 12-13 | 13-14 | 14-15 | 15-16 | 16-17 | 17-18 | 18-19 | 19-20 | 20-21 | 21-22 | 22-23 | 23-0
| Household loads | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0
| Agro Processing Mills | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Saw Mills | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Healthpost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
| Schools | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Street Lights | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1
| Mobile Shops | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
| Bakery Udhyog | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0
| Grill Udhyog | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Poultary Farm | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1
| Usage timetable – Use only if required | 0-1 | 1-2 | 2-3 | 3-4 | 4-5 | 5-6 | 6-7 | 7-8 | 8-9 | 9-10 | 10-11 | 11-12 | 12-13 | 13-14 | 14-15 | 15-16 | 16-17 | 17-18 | 18-19 | 19-20 | 20-21 | 21-22 | 22-23 | 23-0
| Household loads | 0 | 0 | 0 | 30000 | 30000 | 30000 | 30000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 0
| Agro Processing Mills | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Saw Mills | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Healthpost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 0 | 0 | 0 | 0 | 0 | 0
| Schools | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Street Lights | 600 | 600 | 600 | 600 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 600 | 600 | 600 | 600 | 600
| Mobile Shops | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | 0
| Bakery Udhyog | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Grill Udhyog | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 1500 | 1500 | 1500 | 1500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Poultary Farm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total watts (W) | 600 | 600 | 600 | 30600 | 30600 | 30600 | 30000 | 0 | 0 | 2400 | 10904.09 | 10904.09 | 10904.09 | 10904.09 | 10904.09 | 9404.09 | 3400 | 33400 | 30600 | 30600 | 30600 | 30600 | 30600 | 600
| Total watt-hour (Wh) | 600 | 600 | 600 | 30600 | 30600 | 30600 | 30000 | 0 | 0 | 2400 | 10904.09 | 10904.09 | 10904.09 | 10904.09 | 10904.09 | 9404.09 | 3400 | 33400 | 30600 | 30600 | 30600 | 30600 | 30600 | 600

## 3. Report
Basic Solar Minigrid Design | [6 empty] | BOQ Summary | [6 empty] | Single Line Diagram (SLD)
| Name of Designer | Robert Mugabe |  | Organization | RM1as |  |  | Power Generation
| Designation | Engineer |  | Date | 2024-04-12 |  |  | List of Items | Quantity | Unit | Unit Price | Total
| Disclaimer | This basic design serves to estimate the key SMG component sizes and system costs. It shall not be used for detail design and costing. | [5 empty] | Solar Photovoltaic Array of Minimum 415 Wp Capacity where size of individual PV module at least 350Wp, Mono, Mono PERC or Poly Crystalline Silicon. | 41 | kWp | 85 | 3485000 | Npr
| Notes from Designer | [6 empty] | Three Phase PV Inverters with in-built solar MPPT controller of total minimum capacity 20 kW | 2 | Nos | 560000 | 1120000 | Npr
[8 empty] | Off-grid Battery Inverters of total minimum capacity 54 kW, stackable as master and slave for three phase supply. | 9 | Nos | 672400 | 6051600 | Npr
| General Information | [6 empty] | VRLA battery of total minimum capacity 109 kWh (Individual battery capacity should be at least 1000Ah@C10, 2Volt) with rack, cables and accessories. | 109 | kWh | 42300 | 4610700 | Npr
| Name of Beneficiary | Miklajung SMG |  | District | Panchthar |  |  | Solar PV Module support structure, hot dipped galvanized or anodized aluminium metal frame complete set for 41 kWp | 41 | kWp | 18000 | 738000 | Npr
| Name of Chairperson | Rajesh Magar |  | R/Municipality | Sewaroo RM
| Mobile No. | 9812341234 |  | Ward no. | 10 |  |  | Transmission and Distribution
| Province | Koshi Province |  | Tole name | Chilime |  |  | List of Items | Quantity | Unit | Unit Price | Total
Poles
| Technical Information | [6 empty] | Steel Poles | 391 | Nos |  | 8396177.6 | Npr
| PV Array Size(kW) | 41 | kW | NEA grid supply phase | Three Phase |  |  | Cables
| Size of PV Inverter Required(kW) | 40 | kW | Total battery Inverter Size (kW) | 54 | kW |  | Abc cables | 11.7157 | Kms |  | 7545485.4408 | Npr
| Total Transmission and Distribution Length | 11715.6827 | Mtrs | Proximity of NEA grid | 100 | Kms |  | Stay Set | 196 | Nos | 2050 | 401800 | Npr
| Total Battery Bank Capacity Required (kWh) | 109 | kWh |  |  |  |  | Lighting Arrestor | 3 | Nos | 910 | 2730 | Npr
[8 empty] | Ladder | 1 | Nos | 20000 | 20000 | Npr
| Cost of System | [6 empty] | ABC cable accessories (clamps, connectors etc. ) | 1 | Lot | 754548.5441 | 754548.5441 | Npr
| Total cost | 39400349.2238 | NPR | NPR/kWp | 960984.1274 | NPR
| Demand information | [6 empty] | Service Lines for single phase and 3 Phase Customers
| No. Beneficiaries Households | 100 | HH | No. of enterprises | 21 | Nos. |  | Single Phase User
| Household peak load demand | 30 | kW | Productive energy demand | 33.42 | kWh |  | Service Wires | 2 | Kms | 29675 | 59350 | Npr
| Household energy demand | 30 | kWh | Public peak load demand | 5.7541 | kW |  | Meter Box 5 A | 110 | Nos | 6200 | 682000 | Npr
| Productive peak load demand | 19.14 | kW | Public energy demand | 63.0245 | kWh |  | MCB 6 A | 110 | Nos | 760 | 83600 | Npr
3 Phase Customers(PEUs)
[8 empty] | Service Wires | 420 | meters | 29.675 | 12463.5 | Npr
[8 empty] | Meter Box 16 A | 23 | Nos | 11750 | 270250 | Npr
[8 empty] | Meter Box 32 A | 4 | Nos | 6200 | 24800 | Npr
[8 empty] | MCB 6A | 110 | Nos | 760 | 83600 | Npr
[8 empty] | MCB 16A | 23 | Nos | 1100 | 25300 | Npr
[8 empty] | MCB 32A | 4 | Nos | 3122.2222 | 12488.8889 | Npr
[8 empty] | Others (Lamps, streetlights, generation related accessories etc. ) | 1 | lot | 4928718.75 | 4928718.75 | Npr
[8 empty] | Total Cost for the system (inc. of taxes and VAT) | 39400349.2238
[6 empty] | Page 1 of 3 | [6 empty] | Page 2 of 3 |  | Page 3 of 3 | Page 4 of 4
0

## Backend Design
Backend Design
| PV Array Capacity |  |  | Comments and/or supporting information
| Household Load (kW) | 30
| Household Load (kWh) | 30
| PEU load (kW) | 19.14
| PEU load (kWh) | 33.42
| Public Energy Use load(kW) | 5.7541
| Public Energy Use load(kWh) | 63.0245
| Total load (kW) | 54.8941
| Total energy demand per day(kWh) | 126.4445
| Day energy demand (kWh) | 56.9204
| Night energy demand (kWh) | 69.5241
| Select the size of PV module | 415
| Module Efficiency (%) | 17.59
| NOCT (Deg C) | 47
| Tc of Open Circuit Voltage (% / C) | 0.0029
| Tc of Short Circuit Current (% / C) | 0.00048
| Tc of Power (% / C) | 0.0039
| Length x Width x Height (mm x mm x mm) | 1998x1010x35
| Peaksun | 4.5
| PV Array Size(kW) | 41
PV Inverter Sizing
| Size of PV Inverter Required(kW) | 41
| Total inverter size used (kW) | 40
| Individual inverter size (kW) | 20
| No. of PV Inverter Required | 2
Battery Sizing
| Select Battery type | VRLA
| Total Load(Wh) | 69524.09
| Days of Autonomy | 1
| Depth of Discharge | 0.8
| Battery Efficiency | 0.8
| Total Ah Required | 2264
| Battery Bank Voltage(V) | 48
| Total Battery Bank Capacity Required (kWh) | 109
Battery Inverter Sizing
| Total Load (W) | 54894.09
| DC side Voltage(V) | 48
| Rated Power/Unit(W) | 6000
| Total Number of Battery inverters Required | 9
| Total battery Inverter Size (kW) | 54
Cable Sizing-DC
| Module Wiring (Sq.mm) | 2
| Array to Power House (Sq.mm) | 5
MCB/MCCB/O/P For PV inveter
| Total Inverter Size (Watts) | 40000
| Current Draw(Amp) | 58
| Rated Current for MCB(Amp) | 73
| Market Available Size(Amp) | 100
| No.of AC MCB/MCCB required | 2
SMG AC output combiner box
| Is AC combiner box required? | Yes
| Total power from the inveters (AC) | 94000
| Current Draw(Amp) | 136
| Rated Current for MCB(Amp) | 170
| Market Available Size(Amp) | 200
| No.of AC MCB/MCCB required | 2
AC Cable Design
| Inverter to AC combiner Box | 10
| Length of cable per pole (m) | 30
T&D data base
| Capacity of the System(kWp) | Nb of connections | Cable Length | Conn/km | Km/Conn | Km/KW | Conn/KW | Total Cost of the Project | Total T & D Cost
| 316.8 | 700 | 40 | 17.5 | 0.057143 | 0.12626 | 2.2096 | 96258960 | 19585000 | [7 empty] | Select estimation method |  |  | Connection
| 120 | 466 | 37 | 12.5946 | 0.079399 | 0.30833 | 3.8833
| 95 | 280 | 36 | 7.7778 | 0.12857 | 0.37895 | 2.9474 | 46916088 | 14144600 | Method by connection | [9 empty] | Method by capacity
| 50 | 175 | 16 | 10.9375 | 0.091429 | 0.32 | 3.5
| 63.6 | 160 | 32 | 5 | 0.2 | 0.50314 | 2.5157 | 35413242 | 11167400 | Range of categories of connection | [10 empty] | Range of categories of capacity
| 40 | 151 | 13 | 11.6154 | 0.086093 | 0.325 | 3.775 |  |  | From 0 to X X= | From X to Y Y= | [9 empty] | From 0 to X X= | From X to Y Y=
| 55.44 | 140 | 18 | 7.7778 | 0.12857 | 0.32468 | 2.5253 | 30762168 | 8810600 | 40 | 150 | [9 empty] | 30 | 80
| 50 | 139 | 15 | 9.2667 | 0.10791 | 0.3 | 2.78
| 40 | 95 | 2 | 47.5 | 0.021053 | 0.05 | 2.375 |  |  |  |  | Average per category of connection | [10 empty] | Average per category of capacity
| 20 | 80 | 9 | 8.8889 | 0.1125 | 0.45 | 4 |  |  |  |  | Capacity of the System(kWp) | Nb of connections | Cable Length | Conn/km | Km/Conn | Km/KW | Conn/KW |  |  |  |  | Capacity of the System(kWp) | Nb of connections | Cable Length | Conn/km | Km/Conn | Km/KW | Conn/KW
| 21.6 | 66 | 10 | 6.6 | 0.15152 | 0.46296 | 3.0556 | 17831622 | 4309400 | Connection (0- 40) |  | 10.7033 | 29.5 | 2.175 | 18.7589 | 0.075582 | 0.20134 | 2.7859 |  |  | Capacity (0- 30) |  | 15.5477 | 46.7692 | 4.4423 | 16.0555 | 0.089553 | 0.26724 | 3.0311
| 29.7 | 65 | 3.2 | 20.3125 | 0.049231 | 0.10774 | 2.1886 | 18822676 | 1954900 | Connection (40 - 150) |  | 28.334 | 80.5 | 7.97 | 16.0712 | 0.096824 | 0.29408 | 3.0369 |  |  | Capacity (30 - 80) |  | 49.84 | 143.3333 | 16 | 15.3496 | 0.10584 | 0.3038 | 2.9118
| 21.6 | 60 | 12.5 | 4.8 | 0.20833 | 0.5787 | 2.7778 | 17495770 | 4299000 | Connection (150+) |  | 114.2333 | 322 | 29 | 10.9042 | 0.10711 | 0.32695 | 3.1385 |  |  | Capacity (80+) |  | 177.2667 | 482 | 37.6667 | 12.6241 | 0.088371 | 0.27118 | 3.0134
| 15 | 55 | 2 | 27.5 | 0.036364 | 0.13333 | 3.6667
| 15 | 53 | 3 | 17.6667 | 0.056604 | 0.2 | 3.5333
| 15 | 52 | 5 | 10.4 | 0.096154 | 0.33333 | 3.4667
| 10 | 39 | 1.6 | 24.375 | 0.041026 | 0.16 | 3.9 | [8 empty] | General average
| 15 | 38 | 1 | 38 | 0.026316 | 0.066667 | 2.5333 | [8 empty] | Capacity of the System (kWp) | Nb of connections | Cable Length | Conn/km | Km/Conn | Km/KW | Conn/KW
| 12.32 | 35 | 6 | 5.8333 | 0.17143 | 0.48701 | 2.8409 | 12145276 | 2642200 | [6 empty] | 46.9527 | 132.4545 | 12.125 | 15.395 | 0.093835 | 0.27775 | 2.9961
| 10 | 32 | 2 | 16 | 0.0625 | 0.2 | 3.2
| 6.4 | 18 | 1 | 18 | 0.055556 | 0.15625 | 2.8125 | 8778188 | 1158600
| 10.5 | 15 | 1.45 | 10.3448 | 0.096667 | 0.1381 | 1.4286 | 9925837 | 717000

## Backend Values
Backend Values
| Diff.from estimate |  | MCB/MCCB Size (Individual inverter) |  |  |  | Difference from Estimate | Size of the Cable (Sq. mm)
| NA | -67 | 6 | Ampere |  |  | NA | 2.5
| NA | -63 | 10 | Ampere |  |  | NA | 4
| NA | -57 | 16 | Ampere |  |  | NA | 6
| NA | -41 | 32 | Ampere |  |  | 3 | 10
| NA | -10 | 63 | Ampere |  |  | 9 | 16
| 27 | 27 | 100 | Ampere |  |  | 18 | 25
| 127 | 127 | 200 | Ampere |  |  | 28 | 35
| Minimum | 27 |  |  |  |  | 43 | 50
| MCCB Selection | 100 |  |  |  |  | 63 | 70
[7 empty] | 88 | 95
| Diff.from estimate |  | MCB/MCCB Size (AC combiner) |  |  |  | 113 | 120
| NA | -164 | 6 | Ampere |  |  |  | 150
| NA | -160 | 10 | Ampere |  |  | Minimum | 3
| NA | -154 | 16 | Ampere
| NA | -138 | 32 | Ampere |  |  | DC Cable Sizing
| NA | -107 | 63 | Ampere |  |  | Size of Panel | 415
| NA | -70 | 100 | Ampere |  |  | Isc | 10.66
| 30 | 30 | 200 | Ampere |  |  | Vmp | 40.9
| 230 | 230 | 400 | Ampere
| Minimum | 30 |  |  |  |  | Module Wiring | 2
| MCCB Selection | 200 |  |  |  |  | Array to Power House | 5
PV Inverter Selection
| Theoretical inverter size (kW) | 41 | Inverter options (kW) | Current (A)
| 8.2 | 8.2 | 5 | 8.019
| 6.8333 | 6.8333 | 6 | 9.6228
| 5.8571 | 5.8571 | 7 | 11.2266
| 5.125 | 5.125 | 8 | 12.8304
| 4.5556 | 4.5556 | 9 | 14.4342
| 4.1 | 4.1 | 10 | 16.038
| 2.7333 | 2.7333 | 15 | 24.057
| 2.05 | 2.05 | 20 | 32.076
| NA | 1.64 | 25 | 40.0949
| NA | 1.3667 | 30 | 48.1139
| NA | 0.82 | 50 | 80.1899
| NA | 0.41 | 100 | 160.3798
| Minimum: | 2.05
| Roundup: | 2
| Invt. Selected: | 20
| Total inverter size: | 40
Battery inverter selection
| Theoretical battery inverter size (kW) | 54.8941 | Inverter options (kW) | Voltage (V) | Current (A)
| 16.6346 | 16.6346 | 3.3 | 48 | 68.75
| 11.9335 | 11.9335 | 4.6 | 48 | 95.8333
| 9.149 | 9.149 | 6 | 48 | 125
| Minimum: | 9.149
| Roundup: | 9
| Invt. Selected (kW) | 6
| Total inverter size: | 54
Battery Inverter Sizing
| Battery Inverter Required Size(kW) | 54.8941 | Total Peak Power required for battery
| Market Available Inverter Size(kW) | 4.6 | Sunny island 6.0
| No of Theoritical Inverter Required | 11.9335 | Provides the number of theoritical inverter Required |  | Assumption: Max, distance for a string is 32m, 16 modules in series
| No of Set Required | 4 | Provides the multiples of three for battery inverter. |  | Assumption: 16 modules per string
| 1 Set means multiples of 3 | 12 | Provides the total number of inverters required
| Size of Modules | Isc | Imp | VOC | VMP
| 310 | 8.85 | 8.38 | 45.5 | 37
| 315 | 9 | 8.51 | 45.6 | 37.1
| 320 | 9.1 | 8.63 | 45.8 | 37.1
| 325 | 9.25 | 8.76 | 45.9 | 37.2
| 370 | 9.83 | 9.33 | 48.3 | 39.7
| 390 | 10.3 | 9.75 | 48.5 | 40
| 395 | 10.37 | 9.86 | 48.7 | 40.1
| 400 | 12.28 | 11.7 | 41.2 | 34.2
| 405 | 10.52 | 10 | 49.2 | 40.5
| 410 | 10.59 | 10.07 | 49.4 | 40.7
| 415 | 10.66 | 10.15 | 49.6 | 40.9
AC Wire Sizing Chart
Adopted Wire Sizing Formulae
| Wire Size in circular mills = (d*2*I*k)/(V*Vd) |  |  |  | where, | · d = 1-way wire distance
· I = Maximum continuous current rating of the inverter
· V = Nominal utility voltage (i.e. 240, 208 etc.)
· V_d = Percentage voltage drop, for 1% , 0.01
· k = thermal conductivity of the "K- Factor" of a metal; for Copper use 12.9
S.NO
Approximate Wire Sizing
| S.No | AC Wire Description | Length in m | Allowable Voltage Drop | Voltage System (V) |  | Max. Current in Amp | Wire Size in circular mills | Area mm2 | Available Size mm2
| 1 | Inverter to AC combiner Box | 20 | 2 | 400 |  | 136 | 13158 | 7 | 10
| Inverter ratio less than 1.8 has been excluded based on hit-and-trial method to optimize the selection of the inverters | [6 empty] | CM | MM2
[8 empty] | 1 | 0.00050671
| Theoretical inverter size (kW) | 54.8941 | Inverter options (kW) | Current (A) |  | Stay Sets
| 12.4759 | 12.4759 | 4.4 | 6.351 |  |  | No. of Poles | No. of Stay sets | Percentage
| 6.8333 | 6.8333 | 6 | 8.6605 |  |  | 210 | 75 | 35.7143
| 5.125 | 5.125 | 8 | 11.5473 |  |  | 105 | 40 | 38.0952
| 5.125 | 5.125 | 8 | 11.5473 |  |  | 10 | 5 | 50
| 4.5556 | 4.5556 | 9 | 12.9908 |  |  | 275 | 75 | 27.2727
| 4.1 | 4.1 | 10 | 14.4342 |  |  | 90 | 40 | 44.4444
| 2.7333 | 2.7333 | 15 | 21.6513 |  |  | 55 | 25 | 45.4545
| 2.05 | 2.05 | 20 | 28.8684 |  |  | 280 | 100 | 35.7143
| NA | 1.64 | 25 | 36.0855 |  |  | 290 | 100 | 34.4828
| NA | 1.3667 | 30 | 43.3025 |  |  | 30 | 10 | 33.3333
| NA | 0.82 | 50 | 72.1709 |  |  | 16 | 5 | 31.25
| NA | 0.41 | 100 | 144.3418 |  |  | Average |  | 37.5762
| Minimum: | 2.05
| Roundup: | 2
| Invt. Selected: | 20
| Total inverter size: | 40

## Transmission examples
Transmission line examples
Sano Dumre village | 55.4 kWp, 140 HHs, 18km Cable length | Badahare village | 21.6 kWp, 66 HHs, 10 km cable length | Dalaicha Dada | 21.6 kWp, 60 HHs, 12.5 km cable length | Jate Village | 12.32 kWp, 35 HHs, 6km cable length
GPS coordinate 27.371o , 86.696 o |  | GPS coordinate 27.256o , 86.236 o |  | GPS coordinate 27.523o , 86.622 o |  | GPS coordinate 27.284o , 86.377 o
Majhi Tole | 6.4 kWp, 18 HHs, 1 km cable length | Badarjhula | 316.8 kWp, 700 HHs, 40 km cable length | Kakani Village | 63.6 kWp, 160 HHs, 32 km cable length | Mulkharka Village | 95 kWp, 280 HHs, 36 km cable length
GPS coordinate 27.257o , 86.631 o |  | GPS coordinate 27.3651 o , 84.5302 o |  | GPS coordinate 27.284o , 86.377 o |  | GPS coordinate 27.283o , 86.382 o

## Reference Prices
Reference Prices
Components of Bill of Quantities
|  |  | NPR/kWp | 960984.1274
Item No. | Item Description | Quantity | Unit | Rate (NPR) | VAT free | VATable | Total | Remarks
A- Power Generation Components:
1 | Solar PV Modules | 41 | kWp | 85 | 3485000 |  | 3485000 | Taking refernce from KTM district rate
2 | PV Inverter | 2 | Nos | 560000 |  | 1120000 | 1120000 | Taking refernce from market
3 | Battery Inverter | 9 | Nos | 672400 |  | 6051600 | 6051600
4 | VRLA Batteries | 109 | kWh | 42300 |  | 4610700 | 4610700
5 | AC Main distributor with control & protection Accessories | 1 | Set | 3050000 |  | 3050000 | 3050000
6 | Solar PV Module support structure | 41 | Set | 18000 |  | 738000 | 738000
7 | PV Combiner Boxes | 2 | Set | 82500 |  | 165000 | 165000
8 | Off-Grid Combiner Box | 1 | Set | 28000 |  | 28000 | 28000
9 | DC AC copper cables and all accessories complete | 1 | Set | 212000 |  | 212000 | 212000
10 | Earthing System | 1 | Set | 29000 |  | 29000 | 29000
11 | Lightening protection system with accessories | 1 | Set | 156000 |  | 156000 | 156000
12 | Equipotential bonding Bar | 1 | Set | 9000 |  | 9000 | 9000
13 | Three Phase AC SPD | 1 | Nos | 50000 |  | 50000 | 50000
14 | DC SPD | 1 | Nos | 33000 |  | 33000 | 33000
15 | Main Distribution Board | 1 | Nos | 108000 |  | 108000 | 108000
16 | Controll System | 1 | Nos | 680000 |  | 680000 | 680000
17 | Remote Monitoring System | 1 | Nos | 178000 |  | 178000 | 178000
18 | Fire Extenguisher | 1 | Nos | 9100 |  | 9100 | 9100
19 | Exhaust Fan | 1 | Nos | 3300 |  | 3300 | 3300
20 | Office Equipments (Table, Chair, Shelf, Laptop, Printer) | 1 | Set | 130000 |  | 130000 | 130000
| Total Power generation cost: | [5 empty] | 20845700
B. Distribution Components
1 | XLPE Insulated Alumnium Armoured AC Cable (Powerhouse to first pole) | 25 | m | 1212.75 |  | 30318.75 | 30318.75
2 | Earthing System Set for Power Distribution System | 4 | Set | 14500 |  | 58000 | 58000
3 | Distribution Poles (9 m) (80%) | 312.8 | Nos | 21000 |  | 6568800 | 6568800
4 | Distribution Poles (11 m) (20%) | 78.2 | Nos | 23368 |  | 1827377.6 | 1827377.6 | Kailali District rate excluding the transportation cost.
5 | ABC Cables - Main Truck Lines (95 mm2) (20%) | 2.3431 | km | 1212750 |  | 2841638.8381 | 2841638.8381
6 | ABC Cables - Branches (35 mm2) (80%) | 9.3725 | km | 501875 |  | 4703846.6027 | 4703846.6027
7 | ABC cable accessories (clamps, connectors etc. ) | 1 | lot | 754548.5441 |  | 754548.5441 | 754548.5441 | Considered 3 times to the number of poles rate is from AEPC DFS report
8 | Stay Set | 196 | Nos | 2050 |  | 401800 | 401800 | Taking averages from the DFS reports from AEPC
9 | Service Wire | 2 | km | 29675 |  | 59350 | 59350 | Considering 20m wire is required for connection as service wire and rate is considered from the AEPC DFS report
10 | Lighting Arrestor | 3 | Nos | 910 |  | 2730 | 2730 | Considering lighting arrestors are instlled at an inverval of 250m in the poles and the rate is taken from AEPC DFS report
11 | Ladder | 1 | Nos | 20000 |  | 20000 | 20000 | Needed for cleaning and other applications, rate is considered from AEPC Report
12 | Meter 5A | 110 | Nos | 6200 |  | 682000 | 682000 | Considering 10% more meter box more than the number of households and rate is considered from the AEPC DFS report
13 | Meter 16 A | 23 | Nos | 11750 |  | 270250 | 270250 | Considering 10% more MCCB more than the number of households and the rate is considered from AEPC DFS Report
14 | Meter 32 A | 4 | Nos | 6200 |  | 24800 | 24800 | Rate is considered from AEPC Report
15 | MCB 6 A | 110 | Nos | 760 |  | 83600 | 83600
16 | MCB 16 A | 23 | Nos | 1100 |  | 25300 | 25300
17 | MCCB 32 A | 4 | Nos | 3122.2222 |  | 12488.8889 | 12488.8889
18 | Lamp | 600 | Nos | 310 |  | 186000 | 186000 | Considering 6 number of bulbs are required in each households.
19 | Street Light | 1 | Nos | 1800 |  | 1800 | 1800
20 | Tool Box (Insulating Gloves, Crimping Tool, 3-phase Digital Clampmeter etc.) | 2 | Set | 0 |  | 0 | 0
| Total Distrubution cost | [5 empty] | 18554649.2238
| Total Cost for the system | [5 empty] | 39400349.2238
Note: This is BoQ is indicative only. The final BoQ requires Detailed Feasibility Study to be completed.
| Price for on-grid Inverter |  |  |  | Lightning Arrestor
| Available inverter Sizes (Market) |  |  |  | Type | Price | Remarks
| Size | Price |  |  | ESE Type | 85000 | Standard Average Pricing
| 3 | 280000 |  |  | Copper Spike | 5500 | Standard Average Pricing
| 4 | 320000
| 5 | 355000
| 7.5 | 390000
| 9 | 420000
| 12 | 490000
| 15 | 510000
| 20 | 560000
| 25 | 590000
| Price for Battery Inverter |  |  | Available 4 core ABC cables (+10% for connectors), price/meter
| Sunny Island SI 6.0H (4kW) | 603440 |  | Size | Price | Remarks
| Sunny Island SI 8.0H(6kW) | 672400 |  | 25 | 412.5 | Market rate
|  |  |  | 35 | 501.875 | Market rate
| Price for multicluster box |  |  | 50 | 694.375 | Market rate
| Available multicluster box |  |  | 70 | 917.125 | Market rate
| Size | Price |  | 95 | 1212.75 | Market rate
ACDB | 3 | 125000 |  | 10% |  | Accessories
MC | 6 | 790000
MC | 9 | 1160000
MC | 12 | 1160000
MC | 36 | 3050000
Sano Dumre SMG (55.44 kWp) |  |  |  | Badahare SMG (21.4 kWP) |  |  | Majhi Tole SMG (6.4 kWp) |  |  | Badar Jhula SMG (316kWp) |  |  | Dalaicha Dada SMG(21.6 kWp) |  |  | SunKoshi SMG(12.32 kWp) |  |  | Kakani SMG(63.6 kWp) |  |  | Mulkharkha SMG (95 kWp) |  |  | Sumli SMG(29.7 kWp) |  |  | Sangta SMG(10.5 kWp) |  |  | Average
List of Components | Quantity | Unit | Total Cost | Quantity | Unit | Total Cost | Quantity | Unit | Total Cost | Quantity | Unit | Total Cost | Quantity | Unit | Total Cost | Quantity | Unit | Total Cost | Quantity | Unit | Total Cost | Quantity | Unit | Total Cost | Quantity | Unit | Total Cost | Quantity | Unit | Total Cost
Mounting Structure | 55.44 | LS | 100000 | 21.4 | LS | 50000 | 6.4 | LS | 50000 | 316 | LS | 500000 | 21.6 | LS | 50000 | 12.32 | LS | 50000 | 63.6 | LS | 50000 | 95 | LS | 100000 | 29.7 | LS | 504900 | 10.5 | LS | 18000 | 147290
PV Combiner Box | 1 | Set | 75000 | 1 | Set | 75000 | 1 | Set | 75000 | 1 | Set | 75000 | 1 | Set | 75000 | 1 | Set | 75000 | 1 | Set | 75000 | 1 | Set | 75000 | 1 | Set | 150000 | 1 | Set | 75000 | 82500
Off Grid Combiner Box | 1 | Set | 25000 | 1 | Set | 25000 | 1 | Set | 25000 | 1 | Set | 25000 | 1 | Set | 25000 | 1 | Set | 25000 | 1 | Set | 25000 | 1 | Set | 25000 | 1 | Set | 40000 | 1 | Set | 40000 | 28000
DC AC copper cables and all accessories complete | 1 | Set | 350000 | 1 | Set | 350000 | 1 | Set | 200000 | 1 | Set | 200000 | 1 | Set | 200000 | 1 | Set | 200000 | 1 | Set | 200000 | 1 | Set | 200000 | 1 | Set | 110000 | 1 | Set | 110000 | 212000
Earthing System | 1 | Set | 25000 | 1 | Set | 25000 | 1 | Set | 25000 | 1 | Set | 25000 | 1 | Set | 25000 | 1 | Set | 25000 | 1 | Set | 25000 | 1 | Set | 25000 | 1 | Set | 45000 | 1 | Set | 45000 | 29000
Lightening protection system with accessories | 1 | Set | 150000 | 1 | Set | 150000 | 1 | Set | 150000 | 1 | Set | 150000 | 1 | Set | 150000 | 1 | Set | 150000 | 1 | Set | 150000 | 1 | Set | 150000 | 1 | Set | 180000 | 1 | Set | 180000 | 156000
Equipotential bonding Bar | 1 | Nos. | 10000 | 1 | Nos. | 10000 | 1 | Nos. | 10000 | 1 | Nos. | 10000 | 1 | Nos. | 10000 | 1 | Nos. | 10000 | 1 | Nos. | 10000 | 1 | Nos. | 10000 | 1 | Nos. | 5000 | 1 | Nos. | 5000 | 9000
Three Phase AC SPD | 1 | Nos. | 50000 | 1 | Nos. | 50000 | 1 | Nos. | 50000 | 1 | Nos. | 50000 | 1 | Nos. | 50000 | 1 | Nos. | 50000 | 1 | Nos. | 50000 | 1 | Nos. | 50000 | 1 | Nos. | 50000 | 1 | Nos. | 50000 | 50000
DC SPD | 1 | Nos. | 33000 | 1 | Nos. | 33000 | 1 | Nos. | 33000 | 1 | Nos. | 33000 | 1 | Nos. | 33000 | 1 | Nos. | 33000 | 1 | Nos. | 33000 | 1 | Nos. | 33000 | 1 | Nos. | 33000 | 1 | Nos. | 33000 | 33000
Main Distribution Board | 1 | Nos. | 100000 | 1 | Nos. | 100000 | 1 | Nos. | 100000 | 1 | Nos. | 100000 | 1 | Nos. | 100000 | 1 | Nos. | 100000 | 1 | Nos. | 100000 | 1 | Nos. | 100000 | 1 | Nos. | 140000 | 1 | Nos. | 140000 | 108000
Controll System | 1 | LS | 1000000 | 1 | LS | 700000 | 1 | LS | 500000 | 1 | LS | 800000 | 1 | LS | 700000 | 1 | LS | 500000 | 1 | LS | 500000 | 1 | LS | 700000 | 1 | LS | 700000 | 1 | LS | 700000 | 680000
Remote Monitoring System | 1 | Set | 200000 | 1 | Set | 200000 | 1 | Set | 200000 | 1 | Set | 200000 | 1 | Set | 200000 | 1 | Set | 200000 | 1 | Set | 200000 | 1 | Set | 200000 | 1 | Set | 90000 | 1 | Set | 90000 | 178000
Fire Extenguisher | 1 | Set | 15000 | 1 | Set | 15000 | 1 | Set | 7500 | 1 | Set | 7500 | 1 | Set | 7500 | 1 | Set | 7500 | 1 | Set | 7500 | 1 | Set | 7500 | 1 | Set | 8000 | 1 | Set | 8000 | 9100
Exhaust Fan | 1 | Set | 4000 | 1 | Set | 4000 | 1 | Set | 4000 | 1 | Set | 3000 | 1 | Set | 3000 | 1 | Set | 3000 | 1 | Set | 3000 | 1 | Set | 3000 | 1 | Set | 3000 | 1 | Set | 3000 | 3300
| List of Components |  | Sano Dumre SMG (55.44 kWp) |  |  |  | Badahare SMG (21.4 kWP) |  |  |  | Majhi Tole SMG (6.4 kWp) |  |  |  | Badar Jhula SMG (316kWp) |  |  |  | Dalaicha Dada SMG (21.6 kWp) |  |  |  | SunKoshi SMG (12.32 kWp) |  |  |  | Kakani SMG (63.6 kWp) |  |  |  | Mulkharkha SMG (95 kWp) |  |  |  | Sumli SMG (29.7 kWp) |  |  |  | Sangta SMG (10.5 kWp) |  |  |  | Grand Total | Average Unit Cost | Per Unit Cost
|  |  | Quantity | Unit | Unit Cost | Total Cost | Quantity | Unit | Unit Cost | Total Cost | Quantity | Unit | Unit Cost | Total Cost | Quantity | Unit | Unit Cost | Total Cost | Quantity | Unit | Unit Cost | Total Cost | Quantity | Unit | Unit Cost | Total Cost | Quantity | Unit | Unit Cost | Total Cost | Quantity | Unit | Unit Cost | Total Cost | Quantity | Unit | Unit Cost | Total Cost | Quantity | Unit | Unit Cost | Total Cost
| Cable from PH to First Pole |  | 100 | m | 60 | 6000 | 100 | m | 60 | 6000 | 100 | m | 60 | 6000 | 100 | m | 60 | 6000 | 100 | m | 60 | 6000 | 100 | m | 60 | 6000 | 100 | m | 60 | 6000 | 100 | m | 60 | 6000 | 20 | m | 2500 | 50000 | 10 | m | 2500 | 25000 | 123000 | 548 | 60
| Earthing System Set for Power Distribution System |  | 55 | Set | 15000 | 825000 | 25 | Set | 15000 | 375000 | 4 | Set | 15000 | 60000 | 70 | Set | 15000 | 1050000 | 25 | Set | 15000 | 375000 | 15 | Set | 15000 | 225000 | 65 | Set | 15000 | 975000 | 70 | Set | 15000 | 1050000 | 12 | Set | 15000 | 180000 | 5 | Set | 10000 | 50000 | 5165000 | 14500 | 10000
| Distribution Poles (8 m) |  | 210 | Nos | 18000 | 3780000 | 105 | Nos | 18000 | 1890000 | 10 | Nos | 18000 | 180000 | 275 | Nos | 18000 | 4950000 | 90 | Nos | 18000 | 1620000 | 55 | Nos | 18000 | 990000 | 280 | Nos | 18000 | 5040000 | 290 | Nos | 18000 | 5220000 | 20 | Nos | 20000 | 400000 | 13 | Nos | 18000 | 234000 | 24304000 | 18200 | 18000
| Distribution Poles (9 m) | [33 empty] | 10 | Nos | 22000 | 220000 | 3 | Nos | 20000 | 60000 | 280000 | 21000 | 20000
| Distribution Poles (11 m) | [41 empty] | 0 | 23368 | 0
| ACSR Conductor (Rabbit) (50 mm2) |  | 18 | km | 60000 | 1080000 | 10 | km | 60000 | 600000 | 1 | km | 60000 | 60000 | 40 | km | 160000 | 6400000 | 12.5 | km | 60000 | 750000 | 6 | km | 60000 | 360000 | 32 | km | 60000 | 1920000 | 16 | km | 60000 | 960000 | 1.5 | km | 54000 | 81000 | 0 | km |  |  | 12211000 | 70444.4444 | 54000
| ACSR Conductor(Dog) (100 mm2) | [29 empty] | 20 | km | 160000 | 3200000 | [8 empty] | 3200000 | 160000 | 160000
| ACSR Conductor(Squirrel) () | [41 empty] | 0 |  | 0
| ACSR Conductor(Weaseal) (30 mm2) | [33 empty] | 1.7 | km | 42000 | 71400 | 1.5 | km | 38400 | 57600 | 129000 | 40200 | 38400
| Shackle insulators and D-iron (medium size) |  | 440 | Set | 300 | 132000 | 225 | Set | 300 | 67500 | 20 | Set | 300 | 6000 | 900 | Set | 300 | 270000 | 260 | Set | 300 | 78000 | 130 | Set | 300 | 39000 | 700 | Set | 300 | 210000 | 850 | Set | 300 | 255000 | 75 | Set | 300 | 22500 | 45 | Set | 300 | 13500 | 1093500 | 300 | 300
| Stay Set |  | 75 | Set | 2000 | 150000 | 40 | Set | 2000 | 80000 | 5 | Set | 2000 | 10000 | 75 | Set | 2000 | 150000 | 40 | Set | 2000 | 80000 | 25 | Set | 2000 | 50000 | 100 | Set | 2000 | 200000 | 100 | Set | 2000 | 200000 | 10 | Set | 2500 | 25000 | 5 | Set | 2000 | 10000 | 955000 | 2050 | 2000
| Service Wire |  | 4 | km | 30000 | 120000 | 2 | km | 30000 | 60000 | 0.5 | km | 30000 | 15000 | 18 | km | 30000 | 540000 | 2 | km | 30000 | 60000 | 1.5 | km | 30000 | 45000 | 5 | km | 30000 | 150000 | 8 | km | 18750 | 150000 | 2 | km | 35000 | 70000 | 0.4 | km | 33000 | 13200 | 1223200 | 29675 | 18750
| Lighting Arrestor |  | 140 | Pcs | 700 | 98000 | 60 | Pcs | 700 | 42000 | 8 | Pcs | 700 | 5600 | 250 | Pcs | 700 | 175000 | 65 | Pcs | 700 | 45500 | 40 | Pcs | 700 | 28000 | 180 | Pcs | 700 | 126000 | 250 | Pcs | 700 | 175000 | 12 | Pcs | 2000 | 24000 | 5 | Pcs | 1500 | 7500 | 726600 | 910 | 700
| Ladder |  | 1 | Pcs | 20000 | 20000 | 1 | Pcs | 20000 | 20000 | 1 | Pcs | 20000 | 20000 | 1 | Pcs | 20000 | 20000 | 1 | Pcs | 20000 | 20000 | 1 | Pcs | 20000 | 20000 | 1 | Pcs | 20000 | 20000 | 1 | Pcs | 20000 | 20000 | 1 | Pcs | 20000 | 20000 | 1 | Pcs | 20000 | 20000 | 200000 | 20000 | 20000
| Meter 5A |  | 142 | Pcs | 6000 | 852000 | 66 | Pcs | 6000 | 396000 | 20 | Pcs | 6000 | 120000 | 725 | Pcs | 6000 | 4350000 | 60 | Pcs | 6000 | 360000 | 35 | Pcs | 6000 | 210000 | 170 | Pcs | 6000 | 1020000 | 280 | Pcs | 6000 | 1680000 | 65 | Pcs | 7000 | 455000 | 17 | Pcs | 7000 | 119000 | 9562000 | 6200 | 6000
| Meter 32A |  | 4 | Pcs | 12000 | 48000 | 5 | Pcs | 12000 | 60000 | 0 | Pcs |  | 0 | 5 | Pcs | 12000 | 60000 | 5 | Pcs | 12000 | 60000 | 5 | Pcs | 12000 | 60000 | 5 | Pcs | 12000 | 60000 | 10 | Pcs | 12000 | 120000 | 3 | Pcs | 10000 | 30000 | 0 | Pcs |  | 0 | 498000 | 11750 | 10000
| Meter 16 A |  | 4 | Pcs | 6000 | 24000 | 5 | Pcs | 6000 | 30000 | 2 | Pcs | 6000 | 12000 | 5 | Pcs | 6000 | 30000 | 5 | Pcs | 6000 | 30000 | 5 | Pcs | 6000 | 30000 | 5 | Pcs | 6000 | 30000 | 10 | Pcs | 6000 | 60000 | 2 | Pcs | 7000 | 14000 | 1 | Pcs | 7000 | 7000 | 267000 | 6200 | 6000
| MCB 6 A |  | 142 | Pcs | 800 | 113600 | 66 | Pcs | 800 | 52800 | 20 | Pcs | 800 | 16000 | 725 | Pcs | 800 | 580000 | 60 | Pcs | 800 | 48000 | 35 | Pcs | 800 | 28000 | 170 | Pcs | 800 | 136000 | 280 | Pcs | 800 | 224000 | 65 | Pcs | 600 | 39000 | 15 | Pcs | 600 | 9000 | 1246400 | 760 | 600
| MCB 16 A |  | 4 | Pcs | 800 | 3200 | 5 | Pcs | 800 | 4000 | 2 | Pcs | 800 | 1600 | 5 | Pcs | 800 | 4000 | 5 | Pcs | 800 | 4000 | 5 | Pcs | 800 | 4000 | 5 | Pcs | 800 | 4000 | 10 | Pcs | 800 | 8000 | 3 | Pcs | 4000 | 12000 | 2 | Pcs | 600 | 1200 | 46000 | 1100 | 600
| MCCB 32 A |  | 4 | Pcs | 1300 | 5200 | 5 | Pcs | 1300 | 6500 | 0 | Pcs |  | 0 | 5 | Pcs | 1500 | 7500 | 5 | Pcs | 1500 | 7500 | 5 | Pcs | 1500 | 7500 | 5 | Pcs | 1500 | 7500 | 10 | Pcs | 1500 | 15000 | 2 | Pcs | 15000 | 30000 | 1 | Pcs | 3000 | 3000 | 89700 | 3122.2222 | 1300
| Lamp |  | 2 | Pcs | 300 | 600 | 2 | Pcs | 300 | 600 | 2 | Pcs | 300 | 600 | 4 | Pcs | 300 | 1200 | 2 | Pcs | 300 | 600 | 5 | Pcs | 300 | 1500 | 2 | Pcs | 300 | 600 | 2 | Pcs | 300 | 600 | 330 | Pcs | 300 | 99000 | 90 | Pcs | 400 | 36000 | 141300 | 310 | 300
| Street Light |  | 40 | Pcs | 500 | 20000 | 15 | Pcs | 500 | 7500 | 5 | Pcs | 500 | 2500 | 50 | Pcs | 500 | 25000 | 30 | Pcs | 500 | 15000 | 5 | Pcs | 500 | 2500 | 40 | Pcs | 500 | 20000 | 60 | Pcs | 500 | 30000 | 10 | Pcs | 7000 | 70000 | 10 | Pcs | 7000 | 70000 | 262500 | 1800 | 500
| Pyranometer |  | 1 | Set | 600000 | 600000 | 1 | Set | 600000 | 600000 |  | Set |  | 500000 | 1 | Set | 600000 | 600000 | 1 | Set |  | 600000 | 1 | Set |  | 500000 | 1 | Set |  | 600000 | 1 | Set |  | 600000 | 0 | Set |  | 0 | 0 | Set |  | 0 | 4600000 |  | 600000
| Miscellaneous |  |  | LS |  | 933000 |  | LS |  | 11500 |  | LS |  | 143000 |  | LS |  | 6300 | LS | LS |  | 139400 |  | LS |  | 35700 |  | LS |  | 642300 |  | LS |  | 1000 | 0 | LS |  | 0 | 0 | LS |  | 0 | 1912200 |  | 0
| Auto Transformer 50, 25, 40 kVA | [13 empty] | 3 | Pcs |  | 360000 | [12 empty] | 1 | Set |  | 80000 | [8 empty] | 440000 |  | 0
| Tool Box | [34 empty] | Set |  | 40000 |  | Set |  | 35000 | 75000 |  | 0
| Cost of Poles as per Kathmandu district Rate |  |  |  |  | Available Wire Sizes and Prices (Market)-DC Cables; 2C, Unarmoured
| MS Pole 6 m high with rustproof enamel paint dimension 4 inch for buttom 3 m 3 inch for top 3 m |  |  | 17922 |  | Size | Price | Remarks
| MS Pole 7 m high with rustproof enamel paint dimension 4 inch for buttom 4 m 6 inch for top 3 m |  |  | 19776 |  | 2.5 | 103 | Kathmandu District Rate 77/78
| MS Pole 8 m high with rustproof enamel paint dimension 4 inch for buttom 5 m 6 inch for top 3 m |  |  | 22042 |  | 4 | 144 | Kathmandu District Rate 77/78
| MS Pole 9 m high with rustproof enamel paint dimension 4 inch for buttom 6 m 6 inch for top 3 m |  |  | 22351 |  | 6 | 196 | Kathmandu District Rate 77/78
| 7 m Hot Deep Galvanized Pole with Diameter of Pole section 4 inch for bottom 4.5 m and 3 inch for top 2.5 m |  |  | 22042 |  | 10 | 309 | Kathmandu District Rate 77/78
| 8 m Hot Deep Galvanized Pole with Diameter of Pole section 5 inch for bottom 4.5 m, 4 inch for middle 1.75 m and 3 inch for top 1.75 m |  |  | 25441 |  | 16 | 427 | Kathmandu District Rate 77/78
| 9 m Hot Deep Galvanized Pole with Diameter of Pole section 5 inch for bottom 4 inch for middle 2 m and 3 inch for top 2 m |  |  | 27707 |  | 25 | 659 | Kathmandu District Rate 77/78
| 10 m Hot Deep Galvanized Pole with Diameter of Pole section 5 inch for bottom 5.2 m, 4 inch for middle 2.4 m and 3 inch for top 2.4 m |  |  | 29973 |  | 35 | 896 | Kathmandu District Rate 77/78
[6 empty] | 50 | 1236 | Kathmandu District Rate 77/78
[6 empty] | 70 | 1236 | Kathmandu District Rate 77/78
[6 empty] | 95 | 2318 | Kathmandu District Rate 77/78
[6 empty] | 120 | 3039 | Kathmandu District Rate 77/78
[6 empty] | 150 | 3811 | Kathmandu District Rate 77/78
| Available inverter Sizes (Market) |  |  |  |  | Available MCB-TPN/MCCB Sizes and Prices (Market)-25kA
| Size | Price |  |  |  | Size | Price | Remarks
| 3 | 280000 |  |  |  | 6 | 1710 | Kathmandu District Rate 77/78
| 4 | 320000 |  |  |  | 10 | 1710 | Kathmandu District Rate 77/78
| 5 | 355000 |  |  |  | 16 | 1710 | Kathmandu District Rate 77/78
| 7.5 | 390000 |  |  |  | 32 | 6386 | Kathmandu District Rate 77/78
| 9 | 420000 |  |  |  | 63 | 6386 | Kathmandu District Rate 77/78
| 12 | 490000 |  |  |  | 100 | 7045 | Kathmandu District Rate 77/78
| 15 | 510000
| 20 | 560000
| 25 | 590000