## 1. Read Me
Solar Rooftop (SRT) Initial System Planning Tool |  |  | सोलर रूफटप (SRT) प्राथमिक प्रणाली योजना उपकरण
Version |  | 1.1
Developer |  | Nipun Regmi
About | 1 | This design workbook serves as a basic sizing tool to estimate the key On-Grid Solar PV system component sizes and system costs. It shall not be used for detail design and costing. | यो डिजाइन कार्यपुस्तिकाले अन-ग्रिड सौर्य PV प्रणाली कम्पोनेन्ट आकार र प्रणाली लागत अनुमान गर्न आधारभूत साइजिङ उपकरणको रूपमा कार्य गर्दछ। यसलाई विस्तृत डिजाइन र लागतको लागि प्रयोग गरिने छैन।
| 2 | This design workbook uses one particular specificaiton of PV module and Grid Tied Inverter. However, this won't be reflected in the BoQ or have impacts on the design and output. | यस डिजाइन कार्यपुस्तिकाले PV मोड्युल र ग्रिड टाइड इन्भर्टरको एउटा विशेष स्पेसिफिकेशन प्रयोग गरेको छ। यद्यपि, यो BoQ मा प्रतिबिम्बित हुनेछैन वा डिजाइन र आउटपुटमा प्रभाव पार्नेछैन।
| 3 | The designer (or the user) shall only have to enter project data in the 'Inputs' sheet. All other sheets are interlinked and a report is generated in the 'Report' sheet. The designer may update the pricing in the 'Price reference' sheet. | डिजाइनर (वा प्रयोगकर्ता) ले 'Inputs' पानामा मात्र परियोजना डाटा प्रविष्ट गर्नुपर्नेछ। अन्य सबै पानाहरू आपसमा जोडिएका छन् र 'Report' पानामा रिपोर्ट उत्पन्न हुन्छ। डिजाइनरले 'Price reference' पानामा मूल्य निर्धारण अद्यावधिक गर्न सक्छ।
| 4 | The designer may select the Balance of Systems of their choice with simple Required/Not Required function in the 'Inputs' sheet. This will result in inclusion or exclusion of the component in the BoQ. | डिजाइनरले 'Inputs' पानामा आवश्यक छ/आवश्यक छैन प्रकार्यको साथ आफ्नो मनपर्ने प्रणालीहरूको चयन गर्न सक्छ। यसले BoQ मा कम्पोनेन्ट समावेश वा बहिष्कारको परिणाम दिनेछ।
Limitations | 1 | This design workbook is meant to estimate the basic design and cost of the system, detailed design must be done before commencement of project. This design tool is for grid tied system only (with no battery backup) | यो डिजाइन कार्यपुस्तिका प्रणालीको आधारभूत डिजाइन र लागत अनुमान गर्नको लागि मात्र हो। विस्तृत डिजाइन, परियोजना सुरु हुनु अघि गर्नुपर्छ। यो डिजाइन उपकरण Grid connected solar PV प्रणालीको लागि मात्र हो (कुनै ब्याट्री ब्याकअप बिना)
| 2 | The cost of the materials have been included for reference purpose only and not as per the current district rate. The pricelist section must be updated every year and a separate window to enter the pricelist of indicated items must be there in the web design | सामग्रीको मूल्य हालको जिल्ला दर अनुसार Reference प्रयोजनको लागि मात्र समावेश गरिएको छ। Price reference खण्ड प्रत्येक वर्ष अद्यावधिक गरिनुपर्छ।
| 3 | The size of the inverters above 25kW will have inverters size with respect to closest value of multiples of 25kW size inverter only. | 25kW भन्दा माथिको इन्भर्टरको साइजमा 25kW साइजको इन्भर्टरको गुणकको निकटतम मानको सन्दर्भमा इन्भर्टरको साइज हुनेछ।
Assumptions | 1 | The peak sun hours used for the system design is 4.5 kWh/M2 per day; Losses calculated as 30% | प्रणालीको डिजाइनको लागि प्रयोग हुने अधिकतम सूर्य घण्टा 4.5 kWh/M2 प्रति दिन लिएका छौं; घाटा 30% को रूपमा गणना गरिने छ​।
| 2 | Minor components like nut bolts, cable ties, washers, glands, tapes, conduits etc. are taken is lump sum | नट बोल्ट, केबल टाई, धुने, ग्रन्थी, टेप, कन्ड्युइट्स आदि जस्ता साना कम्पोनेन्टहरू एकमुष्ट लिइन्छ।
| 3 | The assumed specifications of the Balance of Systems are described in the 'Price reference' sheet. | प्रणालीको Balance of system अनुमानित विनिर्देशहरू 'Price Reference' पानामा वर्णन गरिएको छ।
| 4 | A contingency of 5% is added before the VAT to the total system cost. | कुल प्रणाली लागतमा VAT अघि 5% को आकस्मिकता थपिएको छ।
Legend | 1 | Inputs to be provided by the user | प्रयोगकर्ताद्वारा प्रदान गरिने इनपुटहरू
| 2 | Dropdown options | ड्रपडाउन विकल्पहरू
| 3 | Recommended default values. Subject to modification, if required. However, alteration require expert knowlede. | प्रस्तावित पूर्वनिर्धारित मूल्यहरू। आवश्यक भएमा परिमार्जन गर्न सकिन्छ। तथापि, परिमार्जन गर्नका लागि विशेषज्ञ ज्ञान आवश्यक छ।
| 4 | Linked cells | लिङ्क गरिएका cells
This tool was produced with funding from the Federal Ministry for Economic Cooperation and Development (BMZ), Germany through Deutsche Gesellschaft für Internationale Zusammenarbeit (GIZ) GmbH.
Published by
The Government of Nepal
Ministry of Energy, Water Resources and Irrigation
Alternative Energy Promotion Centre (AEPC)
Mid Baneshwor, Post Box No.: 14364, Kathmandu, Nepal Tel: +977-1-4498013/4498014
Email: info@aepc.gov.np
Web: www.aepc.gov.np
With support of
Deutsche Gesellschaft für Internationale Zusammenarbeit (GIZ) GmbH
Promotion of Solar Technologies for Economic Development (POSTED) NTNC Complex, Khumaltar, Lalitpur, Nepal
P.O. Box 1457, Kathmandu, Nepal
Tel: +977 1 5555 289, 5538 129
Email: posted@giz.de
Developed by
Integration Umwelt & Energie GmbH, Germany
Author: Nipun Regmi
Review: Ajay Thapa, Kushal Gautam, Muhammed Imran
Layout: Muhammed Imran
March 2024
Password
AEPC-POSTED-SRT-NR

## 2. Inputs
Inputs |  |  | इनपुटहरू
| Benificiary Information |  | प्रयोगकर्ताको विवरण
| Full Name of the Beneficiary | Biratnagar Metropolitan City | प्रयोगकर्ताको पुरा नाम
| Mobile number of the beneficiary | 12 | प्रयोगकर्ताको मोबाइल नम्बर
| Province | Koshi | प्रदेश
| District | Morang | जिल्ला
| Municipality/Rural Municipality | Biratnagar Metropolitan City | नगरपालिका/गाउँपालिका
| Ward No. | 10 | वार्ड नं
| Tole/Locality name | Traffic Chowk | टोल/स्थानीयता नाम
| GPS Coordinates (DMS) | 22.34,83.23 | जीपीएस समन्वयहरू (degrees(°) minutes(') seconds(''))
| Load Type | Commercial | भार प्रकार (औद्योगिक, वाणिज्यिक, आवासीय)
| Installation Type | Rooftop | स्थापना प्रकार (छत माथि, भूमि माउन्ट)
| If rooftop, type of roof | Industrial shed
| DESIGNER INFORMATION |  | डिजाइनरको विवरण
| Full name of designer | Nipun Regmi | डिजाइनरको पूरा नाम
| Designation of the designer | Project Coordinator | डिजाइनरको पद
| Name of the office | POSTED | कार्यालयको नाम
| Date (mm/dd/yyyy) | 2024-03-05 | मिति
| DESIGN INPUTS |  | Comments and/or supporting information (English) | टिप्पणी र/वा सहायक जानकारी (नेपालीमा)
| Total Available Space (Sq. Mtr) | 10000 | Total available space for installation without any shading issues from east and south direction and west facing roof as well as north facing with tilt angle less than 10 degrees. | पूर्व र दक्षिण दिशाबाट कुनै छायांकन समस्याहरू बिना स्थापनाको लागि कुल उपलब्ध ठाउँ
| Max. PV Power W.R.T Area (kW) | 1333.3333 | Assumption: 1kW needs ~10Sq.mtrs of shading free area, inclusive of spaces in between for maintenance and cleaning purposes. RCC roof require 8.5 Sq. m for 1 kWp of DC while 7.5 Sq.m for industrial shed | अनुमान: 1kW लाई ~ 10Sq.mtrs छायांकन मुक्त क्षेत्र चाहिन्छ, मर्मत र सरसफाइ उद्देश्यका लागि बीचमा खाली ठाउँहरू समावेश गरी
| Roof type/Mounting | GI Truss Based Structure | What kind of roof space is available, If installation is to be conducted on rooftop | कस्तो प्रकारको छत उपलब्ध छ, यदि सौर प्यानल छतमा स्थापना गर्ने हो भने
| Azimuth Angle of the Roof (°) | South (180°) | What is the orientation of the available space (North 0°; East90°; South 180°; West 270°) | उपलब्ध ठाउँ कुन दिशा तर्फ अभिमुखीकरण भएको छ
| Required Size of the system (kW) | 100 | The cell will allow the designer to insert input by choosing between Required system size or Available Space for design purpose, based on the selection done at B24 | B24 मा गरिएको छनोटको आधारमा यो सेलले डिजाइनरलाई आवश्यक प्रणाली साइज वा डिजाइन गर्न का लागि उपलब्ध ठाउँको आधारमा, छनोट गरेर Input गर्ने अनुमति दिनेछ।
| Total Height of the building (meters) | 35 | This value will be used to calculate the wind loading requirements for solar support structure ( in the detailed design phase) | यो मान Solar support संरचनाको लागि हावाको लोडिङको आवश्यकताहरू गणना गर्न प्रयोग गरिनेछ (विस्तृत डिजाइन चरणमा)
| Roof Tilt Angle (Degrees) | 25 | This value determines the angle at which the roof is tilted. | यो मानले छत झुकेको कोण निर्धारण गर्छ।
| Grid Supply Phase | Three Phase | This value is required to select between the existing grid supply, either Single Phase or Three Phase | यो मान अवस्थित ग्रिड आपूर्ति, 1-phase वा 3-phase बीच चयन गर्न आवश्यक छ
| Grid Supply Voltage(Volts) | 400 | The voltage level that is available at the evacuation point must be inserted | निकासी बिन्दुमा उपलब्ध भोल्टेज सम्मिलित गर्नु पर्छ
| Distance between Array and Power House (meters) | 50 | This value will be used to calculate the cable sizing requirements | यो मान केबल साइजिङ आवश्यकताहरू गणना गर्न प्रयोग गरिनेछ
| Remote Monitoring Unit | Required | The user can choose an option if they require a Remote Monitoring Unit Or Not | प्रयोगकर्ताले रिमोट मोनिटरिङ युनिट चाहिन्छ वा चाहिदैन भन्ने विकल्प रोज्न सक्छन्
| Bidirectional Energy Meter | Not Required | The user can choose an option if they require a Bidirectional Energy Meter Or Not | प्रयोगकर्ताले Bidirectional ऊर्जा मिटर आवश्यक छ वा छैन भन्ने विकल्प रोज्न सक्छन्
| Solar PV modules | Monocrystalline | The user can choose an option from the drop down menu | प्रयोगकर्ताले solar panel को प्रकारको विकल्प रोज्न सक्छन्
| Reference Solar PV Module (Wp)- Trina Solar | 490 | The user may choose to use a different specification | प्रयोगकर्ताले विभिन्न विशेषिकरण प्रयोग गर्न सक्दछन्
| Vmp (V) | 36.5 | The user may choose to use a different specification | प्रयोगकर्ताले विभिन्न विशेषिकरण प्रयोग गर्न सक्दछन्
| Imp (A) | 13.43 | The user may choose to use a different specification | प्रयोगकर्ताले विभिन्न विशेषिकरण प्रयोग गर्न सक्दछन्
| Voc (V) | 43.4 | The user may choose to use a different specification | प्रयोगकर्ताले विभिन्न विशेषिकरण प्रयोग गर्न सक्दछन्
| Isc (A) | 14.07 | The user may choose to use a different specification | प्रयोगकर्ताले विभिन्न विशेषिकरण प्रयोग गर्न सक्दछन्
| FINANCIAL INPUTS |  | Comments and/or supporting information (English) | टिप्पणी र/वा सहायक जानकारी (नेपालीमा)
| Project Start Year | 2025 | Enter the YEAR on which the project commenced. | परियोजना प्रारम्भ वर्ष
| Project Life (Year) | 25 | Total life of the project | परियोजना जीवनकाल (वर्ष)
| VAT | 13% | Value added Tax | मूल्य अभिवृद्धि कर
| Interest Rate for Loan | 10% | Yearly Interest rate at which the loan maount the have been approved | कर्जाका लागि ब्याज दर
| Exchange rate 1 USD = | 140 | Currency exchange rate from USD to NPR | विनिमय दर

## 3. Report
Report – Basic SRT Design | [6 empty] | Single Line Diagram | [6 empty] | Preliminary Bill of Quantity (BoQ) | [7 empty] | Financials
| Date | 2024-03-05 | [17 empty] | NPR/Wp | 65 | Financial Project Overview | Financing Structure
| Disclaimer | This basic design serves to estimate the key SRT component sizes and system costs. It shall not be used for detail design and costing. | [20 empty] | Source | Value | %
| Notes from Designer | None | [11 empty] | # | Component | Specification | Qty | Units | Unit Cost (NPR.) | Non-Vatable amount (NPR) | Vatable amount (NPR) |  | Developer Equity | 31.1516 | 50%
[14 empty] | 1 | Solar Panel | Monocrystalline | 101 | kWp | 35000 | 3535000 |  |  | Investor Equity | 0 | 0%
| General Information | [12 empty] | 2 | Aluminum Angle | 2x2 Aluminum Frame and relevant Accessories | 101 | kWp | 9000 | 0 | 909000 |  | Grant | 0 | 0%
| Applicant: | Biratnagar Metropolitan City |  | Locality: | Traffic Chowk | [8 empty] | 3 | Grid Connected Inverter | 25 kW | 4 | Pcs. | 590000 | 2360000 | 0 |  | Debt | 31.1516 | 50%
| Mobile No. | 12 |  | GPS Coordinates: | 22.34,83.23 | [8 empty] | 4 | Remote Monitoring Unit | As per the selected inverter | 1 | Pcs. | 65000 | 0 | 65000 |  | Total | 62.3032 | 100%
| Province: | Koshi |  | Designer: | Nipun Regmi | [8 empty] | 5 | Energy Meter | NEA Standard | 0 | Pcs. | 31000 | 0 | 0
| District: | Morang |  | Designation: | Project Coordinator | [8 empty] | 6 | DC Cable (PV Strings) | 4Sq.mm, 1100V, 1 Core | 309 | Meters | 105 | 0 | 32445
| Municipality: | Biratnagar Metropolitan City |  | Office: | POSTED | [8 empty] | 7 | DC Cable(From Array to Power House) | 4 Sq.mm | 50 | Meters | 144 | 0 | 7200
| Ward No.: | 10 | [11 empty] | 8 | AC Cable from String Inverters to AC Combiner Box | 6 Sq.mm, 4 Core, Unarmoured | 40 | Meters | 350 | 0 | 14000
[14 empty] | 9 | DC MCB-String | 20A/1000V | 13 | Pcs. | 3578 | 0 | 46514
| Requirement | [12 empty] | 10 | AC MCB/MCCB-25kA | 63 Amp | 5 | Pcs. | 6386 | 0 | 31930
| System type | Commercial | [11 empty] | 11 | PV Combiner Box | IP66 with in-built SPD | 2 | Pcs. | 10700 | 0 | 21400
| Roof type/Mounting: | GI Truss Based Structure |  | Required Area | 754 | Sq. Mtr | [7 empty] | 12 | Lightning Arrestor | ESE Type | 1 | Pcs. | 85000 | 0 | 85000
| Required Size of the System: | 100 | kWp | Is required Area available? | Yes | [8 empty] | 13 | Earthing rod | Chemical Earthing | 4 | Pcs. | 10000 | 0 | 40000
[14 empty] | 13 | Copper Strip & Insulators | 25 x 5, Approx, 1.5 mtr. =1kg | 27 | kg | 1082 | 0 | 29214
| System Details | [12 empty] | 14 | Installation Accessories | nut bolts, cable tie, tapes, conduits, cable tray etc. | 1 | LS | 606000 | 0 | 606000
| Solar PV Capacity: | 100.45 | kWp | Remote Monitoring: | Present | [8 empty] | 15 | Installation Labor & Transportation | Skilled, Semi-Skilled Technician, Engineer etc. | 1 | Ls | 505000 | 0 | 505000 | Key Performance Indicators | Overall performance |  |  | Overall performance
| Inverter Capacity: | 25 | kW | Generation/Year | 154969.2375 | kWh/Year | [7 empty] | 16 | Contigency-5% | 5% of the total cost | 1 | 0 | 0 | 294750 | 119635.15 |  | Indicator | Value | Unit | Indicator | Value | Unit
| Total Nos. Of inverter: | 4 | Nos. |  |  |  |  | Solar Array: | 100.45 | kW | Solar inverter: | 25 | kW | [5 empty] | Sub-Total | 6189750 | 2512338.15 |  | Project NPV | -68917.199 | $ | LCOE without Grant | 0.099048 | $/kWh
[8 empty] | MCCB: | 63 Amp |  | No. of inverters: | 4 Nos. | [10 empty] | Equity NPV | -57338.1387 | $ | LCOE with Grant | 0.099048 | $/kWh
| Cost | [18 empty] | VAT(13%) | 326603.9595 |  | Project IRR | 0% | % | Minimum DSCR | Less than 1 | ratio
| System Cost (NPR) | 6516353.9595 | NPR | CO2 Emission Avoided | 7749 | kg/year | [16 empty] | Equity IRR | 0% | % | Inflation | 0 | %
| Cost/Wp (NPR) | 65 | NPR/Wp | [10 empty] | Note: This is BoQ is indicative only. The final BoQ requires Detailed Feasibility Study to be completed. | [5 empty] | Grand Total | 6516353.9595 |  | Equity payback | 0 | yrs | Interest Rate | 12% | %
[23 empty] | Discounted (ROI) | -4.252% | %
[5 empty] | Page 1 of 4 | [7 empty] | Page 2 of 4 | [7 empty] | Page 3 of 4 | [6 empty] | Page 4 of 4

## Backend Design
Backend Design
Solar Rooftop Design and Estimation Template |  | Comments and/or supporting information
Requirements | Inputs
Total available rooftop Area (L x B in meters) | 10000
Total System Size (kW) | 100
Type of the rooftop (RCC, CGI Sheet with truss, Others) | GI Truss Based Structure
SOLAR PV SIZING
Option 1: AREA PROVIDED; ASSUMPTION, 1kW = 10Sq. Mtr
Potential solar PV roof top capacity | 1000
Option 2: SOLAR PV SIZE GIVEN ; ASSUMPTION, 1kW = 10Sq. Mtr
Total Solar PV Size Required | 100
SOLAR PV ARRAY SIZING
Total size of the PV System | 100
INVERTER SIZING
Size of the Inverter Required (kW) | 80
Available Inverter Size (kW) | 25
Nos. of Inverter | 4
CABLE SIZING-DC
Module Wiring (mm2) | 4 | Asssumption: Max, distance for a string is 50 mtrs. , 16 in series
Array to Power House | 4 | Assumption: 16 modules per string
MCB/MCCB O/P
Inverter Size (Watts) | 25000
Inverter Size (VA) | 31250
Current Draw (Amp) | 46
Rated Current for MCB (Amp) | 57.5
Market Available Size (Amp) | 63
Nos. Of MCB/MCCB | 5
Solar PV Capacity (kWP)
Nos. of Modules Used | 205
Capacity of each Module (Watts) | 490
System Size (kW) | 100.45
Generation/Year
Size of the PV system(kW) | 100.45
Losses (25%) | 85.3825
Peak Sun Hour | 5.5 | Assumption: A usual value of 4.78 can be considered for Nepal but a 10-15% lower one could be considered as a conservative value.
Generation/Day (kWh) | 469.6037
Generation/Year (330 Days) | 154969.2375
CABLE SIZING-AC
Inverter to AC Combiner Box | 6

## Backend Finance
|  |  |  | Project Year |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
|  |  |  | Calendar Year |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
Backend Finance
| Coordinates | 22.34,83.23
| Site Name | Koshi; Morang; Biratnagar Metropolitan City; 10; Traffic Chowk
| Technology | Solar Rooftop
Project Setup
Key Assumptions
Time Related Parameters
| Project Start Year | 2025
| Start of Loan | 2025
| Baseline beginning year | 1 | #
| Project Life | 25 | years
Currency Related Parameters
| Currency Depreciation | 0% | %
| Discount Rate | 8% | %
Taxation
| VAT | 13% | %
| Income Tax Period 1 | 0% | %
| Duration of Period 1 | 10 | years
| Income Tax Period 2 | 5% | %
| Duration of Perdiod 2 | 5 | years
| Income Tax Period 3 | 25% | %
| Duration of Period | remaining | years
| Other Tax | 0% | %
Grant
| Grant as % of CAPEX | 0% | %
| Project Grant | 0 | USD
| % grant in year 0 | 100% | %
| Project Grant in year 0 | 0 | USD
| % remaining Grant | 0 | %
| Remaining Project Grant | 0 | USD
| Disbursement year of remaining grant | 5 | years
Equity
| Developer Equity | 50% | %
| Investor Equity | 0% | %
| Equity IRR from risk-less investments | 8% | %
Debt
| Normal Project Debt | 50% | %
| Debt Grace Period | 0 | years
| Loan Tenor | 5 | years
| Interest Rate for Loan | 12% | %
Bridge finance
| Remaining Project Grant | 0 | USD
| Bridge Finance Grace Period | 0 | years
| Bridge Finance Tenor | 0 | years
| Interest Rate for Bridge Finance | 0% | %
| Exchange Rate today |  |  |  | Growth Rate | bar: 0 2025 to 25 2050
| 1 USD | 140 | NPR |  | Exchange rate | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140
Expenses
| CAPEX | [7 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
Preliminary Costs
| Project Development | 1000 | USD |  |  | 0 2025: 1000
| Land Acquisition |  | USD |  |  | 0 2025: 0
| Total Preliminary Costs |  |  |  |  | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Generation Assets
| Primary RE generator | Size | 100.45 | kWp
| Solar PV Panels | Assumption of M2 per kWp | 7.5 | M2/kWp
|  | Panel Efficiency | 25% | %
|  | Irradiance GHI | 4.98 | kWh/day·m2
|  | Annual Degradation | 0.6% | %
|  | Solar Panels | 25250 | USD
|  | Lifetime | 26 | years
|  | Replacement Cost | 70% | % |  | 25250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Area Covered By Panels | 753.375 | m2
|  | Energy Generated by Panels | 154969.2375 | kWh/year
| Inverter / converter for primary generator | Size | 100 | kW
| Solar PV Inverter / Converter | Cost NPR | 16857.1429 | USD | 168.5714
|  | Inverter Efficiency | 95% | %
|  | Lifetime | 15 | years
|  | Replacement Cost | 36.22% | % |  | 16857.1429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6105.0792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Primary storage | Size | 0 | kWh
| Battery Storage System | Energy | 0 | kWh/year
|  | Cost | 0 | USD | 0
|  | Lifetime | 16 | years
|  | Replacement Cost | 0.7 | % |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Inverter / converter for primary storage | Size | 0 | kW
| Battery Inverter / Converter | Cost | 0 | USD | 0
|  | Lifetime | 16 | years
|  | Replacement Cost | 0.9 | % |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Secondary generator | Size | 0 | kW
| Diesel Genset (Optional) | Energy | 0 | kWh/year
|  | Cost | 0 | USD | 0
|  | Lifetime | 8 | years
|  | Replacement Cost | 0.9 | % |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Mounting Structure | Size | 100.45 | kW
|  | Cost | 6492.8571 | USD
|  | Lifetime | 26 | years
|  | Replacement Cost | 0.9 | % |  | 6492.8571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Balance of System (BoS) | Total BOS Cost | 5990.4143 | USD |  | 5990.4143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Generation Asset Costs |  |  |  |  | 54590.4143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6105.0792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Distribution Assets | [7 empty] | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
| Poles | Number of new poles | 0 | #
|  | Cost | 0 | USD |  | 0
| Cables | Length of new lines | 399 | m
|  | Cost | 383.1786 | USD |  | 383.1786
| Customer service lines | Number of new connections | 0 | #
|  | Cost | 0 | USD |  | 0
| Other grid equipment | Cost | 0 | USD |  | 0
| Other item | Cost | 0 | USD |  | 0
| Other item | Cost | 0 | USD |  | 0
| Total Distribution Asset Costs |  |  |  |  | 383.1786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Meters | [7 empty] | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
| Single Phase Customer Meters |  | 0 | USD |  | 0
| Three Phase Customer Meters |  | 0 | USD |  | 0
| Other | Totalizers and Other Accessories | 617.1429 | USD |  | 617.1429
| Total Meters Costs |  |  |  |  | 617.1429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Indoor Installations | [7 empty] | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
| Single Phase Customer Installations |  | 0 | USD |  | 0
| Three Phase Customer Installations |  | 0 | USD |  | 0
| Other |  |  | USD |  | 0
| Total Indoor Installation Costs |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| General Costs | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
| Installation |  | 3607.1429 | USD |  | 3607.1429
| Civil Costs |  | 0 | USD |  | 0
| Logistics |  | 0 | USD |  | 0
| Shipping |  | 0 | USD |  | 0
| Customer Acquisition |  | 0 | USD |  | 0
| Travel |  | 0 | USD |  | 0
| Training |  | 0 | USD |  | 0
| Permits |  | 0 | USD |  | 0
| Other | BOS Cost | 2105.3571 | USD |  | 2105.3571
| Total General Costs |  |  |  |  | 5712.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CAPEX factor (for sensitivity analysis) | 100% | %
| TOTAL CAPEX |  |  |  |  | 62303.2357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6105.0792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CAPEX Financing Structure | [7 empty] | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
| Developer Equity |  |  |  |  | 31151.6179
| Investor Equity |  |  |  |  | 0
| Grant |  |  |  |  | 0
| Bridge Finance |  |  |  |  | 0
| Standard Project Loan |  |  |  |  | 31151.6179
| Total Finance |  |  |  |  | 62303.2357
| OPEX Investment | [7 empty] | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
| Diesel Fuel Costs | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
| Diesel Fuel Price |  | 1.5 | USD/litre
| Fuel Usage at Baseline | used only if there is no HOMER timeseries | 0 | litre/year
| Fuel Cost at Baseline |  | 0 | USD/year |  |  | 1.5 | 1.5 | 1.575 | 1.575 | 1.575 | 1.575 | 1.575 | 1.575 | 1.575 | 1.575 | 1.575 | 1.575 | 1.575 | 1.575 | 1.575 | 1.575 | 1.575 | 1.575 | 1.575 | 1.575 | 1.575 | 1.575 | 1.575 | 1.575 | 1.575
| Baseline Cost | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HOMER Modelled Cost | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Considered Cost | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fuel Cost Growth | bar: 1 to 25 25
| Bio Fuel Costs | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
| Bio Fuel Price |  | 0 | USD/litre
| Fuel Usage at Baseline |  | 0 | kg/year |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fuel Cost at Baseline |  | 0 | USD/year |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Considered Cost | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fuel Cost Growth | bar: 1 to 25
| Total Annual Fuel Costs | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Other O&M Costs
| Meter/Monitoring |  | 2500 | USD/year
| Staff |  | 3000 | USD/year
| Insurance |  | 1000 | USD/year
| Other |  |  | USD/year
Other O&M Costs Growth | bar: 1 to 25
| Total Other O&M Costs | [5 empty] | 6630 | 6762.6 | 6897.852 | 7035.809 | 7176.5252 | 7320.0557 | 7466.4568 | 7615.786 | 7768.1017 | 7923.4637 | 8081.933 | 8243.5717 | 8408.4431 | 8576.612 | 8748.1442 | 8923.1071 | 9101.5692 | 9283.6006 | 9469.2726 | 9658.6581 | 9851.8312 | 10048.8679 | 10249.8452 | 10454.8421 | 10663.939
| Grid Usage Fee | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
| Grid Usage Fee per kWh from powerhouse run through network |  | 0 | USD/kWh | bar: 1 to 25
| Grid Usage Fee Over Time |  |  | USD/kWh |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Grid Usage |  |  | USD/year |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Grid Usage Fixed Fee per Annum | optional | 0 | USD/year | bar: 1 to 25
| Total Grid Usage Fee | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Purchases
| Units purchased from DisCo | Base year | 0.01 | kWh/year |  |  | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
| Grid Purchase Price |  | 1e-05 | USD/kWh |  |  | 0% | 2.3% | 0.5% | -1.8% | 0% | 0% | 1% | 0.5% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 5% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Total Grid Purchases | [5 empty] | 1e-07 | 1.023e-07 | 1.0281e-07 | 1.0096e-07 | 1.0096e-07 | 1.0096e-07 | 1.0197e-07 | 1.0248e-07 | 1.0248e-07 | 1.0248e-07 | 1.0248e-07 | 1.0248e-07 | 1.0248e-07 | 1.0248e-07 | 1.0248e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OPEX factor (for sensitivity analysis) | 100% | %
| Total OPEX Expenses | [5 empty] | 6630 | 6762.6 | 6897.852 | 7035.809 | 7176.5252 | 7320.0557 | 7466.4568 | 7615.786 | 7768.1017 | 7923.4637 | 8081.933 | 8243.5717 | 8408.4431 | 8576.612 | 8748.1442 | 8923.1071 | 9101.5692 | 9283.6006 | 9469.2726 | 9658.6581 | 9851.8312 | 10048.8679 | 10249.8452 | 10454.8421 | 10663.939
| Total Expenses |  |  |  |  | 62303.2357 | 6630 | 6762.6 | 6897.852 | 7035.809 | 7176.5252 | 7320.0557 | 7466.4568 | 7615.786 | 7768.1017 | 7923.4637 | 8081.933 | 8243.5717 | 8408.4431 | 8576.612 | 14853.2234 | 8923.1071 | 9101.5692 | 9283.6006 | 9469.2726 | 9658.6581 | 9851.8312 | 10048.8679 | 10249.8452 | 10454.8421 | 10663.939
Revenues
| Commodity / Service Sales | [7 empty] | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Electricity Generation
| Output Energy Electricity in Year 0 | 147220.7756 | kWh/year
| PV Panel Annual Degradation | 0.6% | % per year |  |  |  | 147220.7756 | 146337.451 | 145459.4263 | 144586.6697 | 143719.1497 | 142856.8348 | 141999.6938 | 141147.6956 | 140300.8094 | 139459.0046 | 138622.2506 | 137790.5171 | 136963.774 | 136141.9913 | 135325.1394 | 134513.1885 | 133706.1094 | 132903.8727 | 132106.4495 | 131313.8108 | 130525.9279 | 129742.7724 | 128964.3157 | 128190.5298 | 127421.3867
| Percentage for Self-Consumption | 90% | %
| Units to consider for Energy Savings | 132498.6981 | kWh/year
| Units to consider for Exports | 14722.0776 | kWh/year
| Sales factor (for sensitivity analysis) | 100% | %
| Total Electricity Units | [5 empty] | 147220.7756 | 146337.451 | 145459.4263 | 144586.6697 | 143719.1497 | 142856.8348 | 141999.6938 | 141147.6956 | 140300.8094 | 139459.0046 | 138622.2506 | 137790.5171 | 136963.774 | 136141.9913 | 135325.1394 | 134513.1885 | 133706.1094 | 132903.8727 | 132106.4495 | 131313.8108 | 130525.9279 | 129742.7724 | 128964.3157 | 128190.5298 | 127421.3867
| PV Energy - T.O.D Tariff | Percentage of Energy | Tariff (Rs/kWh) |  |  | Change in Tariff | 0 | 0% | bar: 3 to 25
| Tariff Time 1 (17h -23h) | 5% | 10.5 |  |  | Revenues from Energy Savings | 8184.1607 | 8135.0557 | 8086.2454 | 8037.7279 | 7989.5015 | 7941.5645 | 7893.9151 | 7846.5516 | 7799.4723 | 7752.6755 | 7706.1594 | 7659.9225 | 7613.9629 | 7568.2792 | 7522.8695 | 7477.7323 | 7432.8659 | 7388.2687 | 7343.9391 | 7299.8754 | 7256.0762 | 7212.5397 | 7169.2645 | 7126.2489 | 7083.4914
| Tariff Time 2 (23h - 05h) | 0% | 5.4
| Tarif Time 3 (05h - 17h) | 95% | 8.55
[6 empty] | Change in Tariff | 0 | 0% | bar: 3 to 25
| Average Tariff To Consider for Energy Savings | 8.6475 | Rs/kWh |  |  | Revenues From Energy Exports | 624.6367 | 620.8889 | 617.1636 | 613.4606 | 609.7798 | 606.1211 | 602.4844 | 598.8695 | 595.2763 | 591.7046 | 588.1544 | 584.6255 | 581.1177 | 577.631 | 574.1652 | 570.7202 | 567.2959 | 563.8921 | 560.5088 | 557.1457 | 553.8029 | 550.48 | 547.1772 | 543.8941 | 540.6307
| Tariff Energy Exports (NEA Net-Metering) | 5.94 | Rs/kWh
| PPA Rate (Only Populate for ESCO Model) | 0 | Rs/kWh | (if no PPA, insert 0)
| Total Electricity Revenues | [5 empty] | 8808.7974 | 8755.9446 | 8703.4089 | 8651.1885 | 8599.2813 | 8547.6856 | 8496.3995 | 8445.4211 | 8394.7486 | 8344.3801 | 8294.3138 | 8244.548 | 8195.0807 | 8145.9102 | 8097.0347 | 8048.4525 | 8000.1618 | 7952.1608 | 7904.4479 | 7857.0212 | 7809.879 | 7763.0198 | 7716.4417 | 7670.143 | 7624.1221
| Grants | [7 empty] | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
| Grant as % of CAPEX | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
| Total Amount of Grant |  | 0 | USD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Generation Based Subsidy
| Generation Subsidy | 0 | Rs/kWh |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Duration of Subsidy | 0 | years
Vat-exemptions
| Amount to be exempt | 0 | USD | add cost for all vat exempt values excl. Panels & Inverters
| VAT | 13% | % |  |  | 0
Interest Buy-Down Grant
| Percentage of Buy-Down | 50% | % |  |  | 0 | 1869.0971 | 1574.883 | 1245.3632 | 876.3011 | 462.9515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Duration of Subsidy | 5 | years
| Total Grant |  |  |  |  | 0 | 1869.0971 | 1574.883 | 1245.3632 | 876.3011 | 462.9515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Revenues |  |  |  |  | 0 | 10677.8944 | 10330.8276 | 9948.7722 | 9527.4896 | 9062.2329 | 8547.6856 | 8496.3995 | 8445.4211 | 8394.7486 | 8344.3801 | 8294.3138 | 8244.548 | 8195.0807 | 8145.9102 | 8097.0347 | 8048.4525 | 8000.1618 | 7952.1608 | 7904.4479 | 7857.0212 | 7809.879 | 7763.0198 | 7716.4417 | 7670.143 | 7624.1221
Expenses
| Annual Operational Costs |  |  |  |  | 0 | 6630 | 6762.6 | 6897.852 | 7035.809 | 7176.5252 | 7320.0557 | 7466.4568 | 7615.786 | 7768.1017 | 7923.4637 | 8081.933 | 8243.5717 | 8408.4431 | 8576.612 | 8748.1442 | 8923.1071 | 9101.5692 | 9283.6006 | 9469.2726 | 9658.6581 | 9851.8312 | 10048.8679 | 10249.8452 | 10454.8421 | 10663.939
| Investments for Power Generation Assets |  |  |  |  | 54590.4143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6105.0792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Investments for Power Distribution Assets |  |  |  |  | 383.1786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Investment for Meters |  |  |  |  | 617.1429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Investments for Indoor Installations |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Project Development & General Costs |  |  |  |  | 6712.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Expenditures |  |  | 280769.2021 |  | 62303.2357 | 6630 | 6762.6 | 6897.852 | 7035.809 | 7176.5252 | 7320.0557 | 7466.4568 | 7615.786 | 7768.1017 | 7923.4637 | 8081.933 | 8243.5717 | 8408.4431 | 8576.612 | 14853.2234 | 8923.1071 | 9101.5692 | 9283.6006 | 9469.2726 | 9658.6581 | 9851.8312 | 10048.8679 | 10249.8452 | 10454.8421 | 10663.939
Revenues
| Revenue from Electricity Sales | [5 empty] | 8808.7974 | 8755.9446 | 8703.4089 | 8651.1885 | 8599.2813 | 8547.6856 | 8496.3995 | 8445.4211 | 8394.7486 | 8344.3801 | 8294.3138 | 8244.548 | 8195.0807 | 8145.9102 | 8097.0347 | 8048.4525 | 8000.1618 | 7952.1608 | 7904.4479 | 7857.0212 | 7809.879 | 7763.0198 | 7716.4417 | 7670.143 | 7624.1221
| Revenue from Grants |  |  |  |  | 0 | 1869.0971 | 1574.883 | 1245.3632 | 876.3011 | 462.9515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
| Total Revenues |  |  | 211098.6889 |  | 0 | 10677.8944 | 10330.8276 | 9948.7722 | 9527.4896 | 9062.2329 | 8547.6856 | 8496.3995 | 8445.4211 | 8394.7486 | 8344.3801 | 8294.3138 | 8244.548 | 8195.0807 | 8145.9102 | 8097.0347 | 8048.4525 | 8000.1618 | 7952.1608 | 7904.4479 | 7857.0212 | 7809.899 | 7763.0398 | 7716.4617 | 7670.163 | 7624.1421
| Total Revenues (Project Life) | 211098.5889 | USD
| Total Expenses (Project Life) | 280769.2021 | USD
| CAPEX | 62303.2357 | USD
Depreciation and Reinvestment
| Depreciation (linear) |  |  |  | Calendar Year | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
|  | Upfront Cost (For Depreciation) | Replacement Cost |  | Asset to be Depreciated | 2025: Depreciation Duration
Generation Assets
| Solar PV Panels | 25250 | 17675 |  | Yes | 25 | 1010 | 1010 | 1010 | 1010 | 1010 | 1010 | 1010 | 1010 | 1010 | 1010 | 1010 | 1010 | 1010 | 1010 | 1010 | 1010 | 1010 | 1010 | 1010 | 1010 | 1010 | 1010 | 1010 | 1010 | 1010
| Solar PV Inverter / Converter | 16857.1429 | 6105.0792 |  | Yes | 15 | 1123.8095 | 1123.8095 | 1123.8095 | 1123.8095 | 1123.8095 | 1123.8095 | 1123.8095 | 1123.8095 | 1123.8095 | 1123.8095 | 1123.8095 | 1123.8095 | 1123.8095 | 1123.8095 | 1123.8095 | 407.0053 | 407.0053 | 407.0053 | 407.0053 | 407.0053 | 407.0053 | 407.0053 | 407.0053 | 407.0053 | 407.0053
| Battery Storage System | 0 | 0 |  | Yes | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Battery Inverter / Converter | 0 | 0 |  | Yes | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diesel Genset (Optional) | 0 | 0 |  | Yes | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Mounting Structure | 6492.8571 | 5843.5714 |  | Yes | 26 | 249.7253 | 249.7253 | 249.7253 | 249.7253 | 249.7253 | 249.7253 | 249.7253 | 249.7253 | 249.7253 | 249.7253 | 249.7253 | 249.7253 | 249.7253 | 249.7253 | 249.7253 | 249.7253 | 249.7253 | 249.7253 | 249.7253 | 249.7253 | 249.7253 | 249.7253 | 249.7253 | 249.7253 | 249.7253
| Balance of System (BoS) | 5990.4143 | 0 |  | Yes | 25 | 239.6166 | 239.6166 | 239.6166 | 239.6166 | 239.6166 | 239.6166 | 239.6166 | 239.6166 | 239.6166 | 239.6166 | 239.6166 | 239.6166 | 239.6166 | 239.6166 | 239.6166 | 239.6166 | 239.6166 | 239.6166 | 239.6166 | 239.6166 | 239.6166 | 239.6166 | 239.6166 | 239.6166 | 239.6166
Distribution Assets
| Poles | 0 |  |  | Yes | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cables | 383.1786 |  |  | Yes | 25 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271
| Customer service lines | 0 |  |  | Yes | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other grid equipment | 0 |  |  | Yes | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other item | 0 |  |  | Yes | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other item | 0 |  |  | Yes | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Meters
| Single Phase Customer Meters | 0 |  |  | Yes | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Three Phase Customer Meters | 0 |  |  | No | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 617.1429 |  |  | Yes | 25 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857
Indoor Installations
| Single Phase Customer Installations | 0 |  |  | Yes | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Three Phase Customer Installations | 0 |  |  | Yes | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 0 |  |  | Yes | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Depreciation of Assets | 55590.7357 |  |  |  |  | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 1946.36 | 1946.36 | 1946.36 | 1946.36 | 1946.36 | 1946.36 | 1946.36 | 1946.36 | 1946.36 | 1946.36
| Reinvestment |  |  |  | Year | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Solar PV Panels | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Solar PV Inverter / Converter | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6105.0792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Battery Storage System | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Battery Inverter / Converter | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diesel Genset (Optional) | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Mounting Structure | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Reinvestments | 6105.0792 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6105.0792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Remaining Value of Assets | [5 empty] | 52927.5715 | 50264.4073 | 47601.243 | 44938.0788 | 42274.9146 | 39611.7504 | 36948.5861 | 34285.4219 | 31622.2577 | 28959.0934 | 26295.9292 | 23632.765 | 20969.6008 | 18306.4365 | 21748.3515 | 19801.9915 | 17855.6316 | 15909.2716 | 13962.9116 | 12016.5516 | 10070.1916 | 8123.8316 | 6177.4717 | 4231.1117 | 2284.7517
| Standard Project Debt Service Plan |  |  |  | Year | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Loan Opening Balance |  |  |  |  | 31151.6179 | 31151.6179 | 26248.05 | 20756.0541 | 14605.0186 | 7715.8589 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12
| Principal Repayment |  |  |  |  | 0 | 4903.5678 | 5491.996 | 6151.0355 | 6889.1597 | 7715.8589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Standard Loan Interest Expenses |  |  |  |  | 0 | 3738.1941 | 3149.766 | 2490.7265 | 1752.6022 | 925.9031 | -5.457e-13 | -5.457e-13 | -5.457e-13 | -5.457e-13 | -5.457e-13 | -5.457e-13 | -5.457e-13 | -5.457e-13 | -5.457e-13 | -5.457e-13 | -5.457e-13 | -5.457e-13 | -5.457e-13 | -5.457e-13 | -5.457e-13 | -5.457e-13 | -5.457e-13 | -5.457e-13 | -5.457e-13 | -5.457e-13
| Loan Closing Balance |  |  |  |  | 31151.6179 | 26248.05 | 20756.0541 | 14605.0186 | 7715.8589 | 0 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12
| Bridge Finance Debt Service Plan |  |  |  | Year | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Loan Opening Balance |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Principal Repayment |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Bridge Finance Interest Expenses |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Loan Closing Balance |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Company Performance
|  |  |  | Project Year |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
|  |  |  | Calendar Year |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Income Statement | [20 empty] | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Electricity Sales
| Revenue From Energy Savings | [5 empty] | 8184.1607 | 8135.0557 | 8086.2454 | 8037.7279 | 7989.5015 | 7941.5645 | 7893.9151 | 7846.5516 | 7799.4723 | 7752.6755 | 7706.1594 | 7659.9225 | 7613.9629 | 7568.2792 | 7522.8695 | 7477.7323 | 7432.8659 | 7388.2687 | 7343.9391 | 7299.8754 | 7256.0762 | 7212.5397 | 7169.2645 | 7126.2489 | 7083.4914
| Revenue from Energy Sales | [5 empty] | 624.6367 | 620.8889 | 617.1636 | 613.4606 | 609.7798 | 606.1211 | 602.4844 | 598.8695 | 595.2763 | 591.7046 | 588.1544 | 584.6255 | 581.1177 | 577.631 | 574.1652 | 570.7202 | 567.2959 | 563.8921 | 560.5088 | 557.1457 | 553.8029 | 550.48 | 547.1772 | 543.8941 | 540.6307
| Total Gross Revenues | [5 empty] | 8808.7974 | 8755.9446 | 8703.4089 | 8651.1885 | 8599.2813 | 8547.6856 | 8496.3995 | 8445.4211 | 8394.7486 | 8344.3801 | 8294.3138 | 8244.548 | 8195.0807 | 8145.9102 | 8097.0347 | 8048.4525 | 8000.1618 | 7952.1608 | 7904.4479 | 7857.0212 | 7809.879 | 7763.0198 | 7716.4417 | 7670.143 | 7624.1221
Electricity Purchases
| Energy Purchased from DisCo | [5 empty] | 1e-07 | 1.023e-07 | 1.0281e-07 | 1.0096e-07 | 1.0096e-07 | 1.0096e-07 | 1.0197e-07 | 1.0248e-07 | 1.0248e-07 | 1.0248e-07 | 1.0248e-07 | 1.0248e-07 | 1.0248e-07 | 1.0248e-07 | 1.0248e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Purchases | [5 empty] | 1e-07 | 1.023e-07 | 1.0281e-07 | 1.0096e-07 | 1.0096e-07 | 1.0096e-07 | 1.0197e-07 | 1.0248e-07 | 1.0248e-07 | 1.0248e-07 | 1.0248e-07 | 1.0248e-07 | 1.0248e-07 | 1.0248e-07 | 1.0248e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net Revenues | [5 empty] | 8808.7974 | 8755.9446 | 8703.4089 | 8651.1885 | 8599.2813 | 8547.6856 | 8496.3995 | 8445.4211 | 8394.7486 | 8344.3801 | 8294.3138 | 8244.548 | 8195.0807 | 8145.9102 | 8097.0347 | 8048.4525 | 8000.1618 | 7952.1608 | 7904.4479 | 7857.0212 | 7809.879 | 7763.0198 | 7716.4417 | 7670.143 | 7624.1221
VAT
| VAT on Net Revenues | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003.1374 | 997.1186 | 991.1359
| Total Revenues Net of VAT | [5 empty] | 8808.7974 | 8755.9446 | 8703.4089 | 8651.1885 | 8599.2813 | 8547.6856 | 8496.3995 | 8445.4211 | 8394.7486 | 8344.3801 | 8294.3138 | 8244.548 | 8195.0807 | 8145.9102 | 8097.0347 | 8048.4525 | 8000.1618 | 7952.1608 | 7904.4479 | 7857.0212 | 7809.879 | 7763.0198 | 6713.3042 | 6673.0244 | 6632.9863
Currency Depreciation
| Revenues Adjusted for Currency Depreciation | [5 empty] | 8808.7974 | 8755.9446 | 8703.4089 | 8651.1885 | 8599.2813 | 8547.6856 | 8496.3995 | 8445.4211 | 8394.7486 | 8344.3801 | 8294.3138 | 8244.548 | 8195.0807 | 8145.9102 | 8097.0347 | 8048.4525 | 8000.1618 | 7952.1608 | 7904.4479 | 7857.0212 | 7809.879 | 7763.0198 | 6713.3042 | 6673.0244 | 6632.9863
Operating Costs
| Fuel Cost | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other O&M Costs | [5 empty] | 6630 | 6762.6 | 6897.852 | 7035.809 | 7176.5252 | 7320.0557 | 7466.4568 | 7615.786 | 7768.1017 | 7923.4637 | 8081.933 | 8243.5717 | 8408.4431 | 8576.612 | 8748.1442 | 8923.1071 | 9101.5692 | 9283.6006 | 9469.2726 | 9658.6581 | 9851.8312 | 10048.8679 | 10249.8452 | 10454.8421 | 10663.939
| Grid usage fee | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total OPEX | [5 empty] | 6630 | 6762.6 | 6897.852 | 7035.809 | 7176.5252 | 7320.0557 | 7466.4568 | 7615.786 | 7768.1017 | 7923.4637 | 8081.933 | 8243.5717 | 8408.4431 | 8576.612 | 8748.1442 | 8923.1071 | 9101.5692 | 9283.6006 | 9469.2726 | 9658.6581 | 9851.8312 | 10048.8679 | 10249.8452 | 10454.8421 | 10663.939
| EBITDA |  |  |  |  | 0 | 2178.7974 | 1993.3446 | 1805.5569 | 1615.3794 | 1422.7561 | 1227.6299 | 1029.9427 | 829.6352 | 626.6469 | 420.9164 | 212.3808 | 0.97629 | -213.3624 | -430.7018 | -651.1095 | -874.6546 | -1101.4074 | -1331.4398 | -1564.8248 | -1801.6369 | -2041.9522 | -2285.8481 | -3536.541 | -3781.8177 | -4030.9527
Depreciation
| Generation Assets | [5 empty] | 2623.1514 | 2623.1514 | 2623.1514 | 2623.1514 | 2623.1514 | 2623.1514 | 2623.1514 | 2623.1514 | 2623.1514 | 2623.1514 | 2623.1514 | 2623.1514 | 2623.1514 | 2623.1514 | 2623.1514 | 1906.3471 | 1906.3471 | 1906.3471 | 1906.3471 | 1906.3471 | 1906.3471 | 1906.3471 | 1906.3471 | 1906.3471 | 1906.3471
| Distribution Assets | [5 empty] | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271 | 15.3271
| Meters | [5 empty] | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857 | 24.6857
| Indoor Installations | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Depreciation of Assets | [5 empty] | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 1946.36 | 1946.36 | 1946.36 | 1946.36 | 1946.36 | 1946.36 | 1946.36 | 1946.36 | 1946.36 | 1946.36
| EBIT | [5 empty] | -484.3669 | -669.8196 | -857.6073 | -1047.7848 | -1240.4081 | -1435.5343 | -1633.2215 | -1833.5291 | -2036.5173 | -2242.2478 | -2450.7834 | -2662.1879 | -2876.5267 | -3093.866 | -3314.2737 | -2821.0146 | -3047.7674 | -3277.7998 | -3511.1847 | -3747.9969 | -3988.3122 | -4232.2081 | -5482.901 | -5728.1777 | -5977.3127
Interest
| Bridge Finance Financing Period |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
| Bridge Finance Principal Repayment Period |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
| Bridge Finance Principal Repayment Period |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Standard Project Loan Financing Period |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
| Standard Project Loan Principal Repayment Period |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
| Standard Project Loan Principal Repayment Period |  |  |  |  | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total CAPEX Required |  |  |  |  | 0 0: 62303.2357
| Developer Equity |  |  |  |  | 0 0: 31151.6179
| Investor Equity |  |  |  |  | 0 0: 0
| Grant |  |  |  |  | 0 0: 0
| Bridge Finance |  |  |  |  | 0 0: 0
| Loan Opening Balance |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Principal Repayment | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Loan Closing Balance |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Bridge Finance Interest Expenses | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Standard Project Loan |  |  |  |  | 0 0: 31151.6179
| Loan Opening Balance |  |  |  |  | 31151.6179 | 31151.6179 | 26248.05 | 20756.0541 | 14605.0186 | 7715.8589 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12
| Principal Repayment | [5 empty] | 4903.5678 | 5491.996 | 6151.0355 | 6889.1597 | 7715.8589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Loan Closing Balance |  |  |  |  | 31151.6179 | 26248.05 | 20756.0541 | 14605.0186 | 7715.8589 | 0 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12
| Standard Loan Interest Expenses | [5 empty] | 3738.1941 | 3149.766 | 2490.7265 | 1752.6022 | 925.9031 | -5.457e-13 | -5.457e-13 | -5.457e-13 | -5.457e-13 | -5.457e-13 | -5.457e-13 | -5.457e-13 | -5.457e-13 | -5.457e-13 | -5.457e-13 | -5.457e-13 | -5.457e-13 | -5.457e-13 | -5.457e-13 | -5.457e-13 | -5.457e-13 | -5.457e-13 | -5.457e-13 | -5.457e-13 | -5.457e-13
| EBT |  |  |  |  | 0 | -4222.561 | -3819.5856 | -3348.3338 | -2800.387 | -2166.3112 | -1435.5343 | -1633.2215 | -1833.5291 | -2036.5173 | -2242.2478 | -2450.7834 | -2662.1879 | -2876.5267 | -3093.866 | -3314.2737 | -2821.0146 | -3047.7674 | -3277.7998 | -3511.1847 | -3747.9969 | -3988.3122 | -4232.2081 | -5482.901 | -5728.1777 | -5977.3127
Taxes
| Depreciation + EBT | [5 empty] | -1559.3968 | -1156.4214 | -685.1696 | -137.2228 | 496.853 | 1227.6299 | 1029.9427 | 829.6352 | 626.6469 | 420.9164 | 212.3808 | 0.97629 | -213.3624 | -430.7018 | -651.1095 | -874.6546 | -1101.4074 | -1331.4398 | -1564.8248 | -1801.6369 | -2041.9522 | -2285.8481 | -3536.541 | -3781.8177 | -4030.9527
| Tax incentive 2 : Capital Allowance | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Remaining available allowance |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Tax Incentives 3: Loss Relief | [5 empty] | 0 | 4222.561 | 3819.5856 | 3348.3338 | 2800.387 | 2166.3112 | 1435.5343 | 1633.2215 | 1833.5291 | 2036.5173 | 2242.2478 | 2450.7834 | 2662.1879 | 2876.5267 | 3093.866 | 3314.2737 | 2821.0146 | 3047.7674 | 3277.7998 | 3511.1847 | 3747.9969 | 3988.3122 | 4232.2081 | 5482.901 | 5728.1777
| Total Tax incentives | [5 empty] | 0 | 4222.561 | 3819.5856 | 3348.3338 | 2800.387 | 2166.3112 | 1435.5343 | 1633.2215 | 1833.5291 | 2036.5173 | 2242.2478 | 2450.7834 | 2662.1879 | 2876.5267 | 3093.866 | 3314.2737 | 2821.0146 | 3047.7674 | 3277.7998 | 3511.1847 | 3747.9969 | 3988.3122 | 4232.2081 | 5482.901 | 5728.1777
| Taxable Income (Depreciation + EBT - Tax Incentives) | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Income Tax | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Tax Holiday Period 1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Tax Holiday Period 2 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other Tax | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Taxes | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net Income | [5 empty] | -4222.561 | -3819.5856 | -3348.3338 | -2800.387 | -2166.3112 | -1435.5343 | -1633.2215 | -1833.5291 | -2036.5173 | -2242.2478 | -2450.7834 | -2662.1879 | -2876.5267 | -3093.866 | -3314.2737 | -2821.0146 | -3047.7674 | -3277.7998 | -3511.1847 | -3747.9969 | -3988.3122 | -4232.2081 | -5482.901 | -5728.1777 | -5977.3127
Cashflow Statement
| Operational Cashflow |  |  |  |  | 20 20: -3747.9969
| Net Income |  |  |  | -81750.5413 |  | -4222.561 | -3819.5856 | -3348.3338 | -2800.387 | -2166.3112 | -1435.5343 | -1633.2215 | -1833.5291 | -2036.5173 | -2242.2478 | -2450.7834 | -2662.1879 | -2876.5267 | -3093.866 | -3314.2737 | -2821.0146 | -3047.7674 | -3277.7998 | -3511.1847 | -3747.9969 | -3988.3122 | -4232.2081 | -5482.901 | -5728.1777 | -5977.3127
| Depreciation | [5 empty] | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 1946.36 | 1946.36 | 1946.36 | 1946.36 | 1946.36 | 1946.36 | 1946.36 | 1946.36 | 1946.36 | 1946.36
| Total Operational Cashflow |  |  |  |  | 0 | -1559.3968 | -1156.4214 | -685.1696 | -137.2228 | 496.853 | 1227.6299 | 1029.9427 | 829.6352 | 626.6469 | 420.9164 | 212.3808 | 0.97629 | -213.3624 | -430.7018 | -651.1095 | -874.6546 | -1101.4074 | -1331.4398 | -1564.8248 | -1801.6369 | -2041.9522 | -2285.8481 | -3536.541 | -3781.8177 | -4030.9527
Grant Cashflow
| Total Grant Cashflow |  |  |  |  | 0 | 1869.0971 | 1574.883 | 1245.3632 | 876.3011 | 462.9515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Initial Investment Cashflow |  |  |  |  | 20 20: -3747.9969
| Developer Equity |  |  |  |  | 0 0: -31151.6179
| Investor Equity |  |  |  |  | 0 0: 0
| Grant |  |  |  |  | 0 0: 0
| Bridge Finance |  |  |  |  | 0 0: 0
| Standard Project Loan |  |  |  |  | 0 0: -31151.6179
| Total Initial Investment |  |  |  |  | -62303.2357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Reinvestment Cashflow
| Solar PV Panels |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Solar PV Inverter / Converter |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6105.0792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Battery Storage System |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Battery Inverter / Converter |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diesel Genset (Optional) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Mounting Structure |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Reinvestments |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6105.0792 | 0 | 0 | 0 | 0 | 0
| Total Investing Cashflow |  |  |  |  | -62303.2357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6105.0792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cashflow for project IRR calculation (operational cashflow - reinvestments) |  |  |  |  | -62303.2357 | -1559.3968 | -1156.4214 | -685.1696 | -137.2228 | 496.853 | 1227.6299 | 1029.9427 | 829.6352 | 626.6469 | 420.9164 | 212.3808 | 0.97629 | -213.3624 | -430.7018 | -6756.1887 | -874.6546 | -1101.4074 | -1331.4398 | -1564.8248 | -1801.6369 | -2041.9522 | -2285.8481 | -3536.541 | -3781.8177 | -4030.9527
Financing Cashflow
| Bridge Finance Financing |  |  |  |  | 0 0: 0
| Bridge Finance Principal Repayment |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Standard Project Debt Financing |  |  |  |  | 0 0: 31151.6179
| Standard Project Debt Principal Repayment |  |  |  |  | 0 | -4903.5678 | -5491.996 | -6151.0355 | -6889.1597 | -7715.8589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Financing Cashflow |  |  |  |  | 31151.6179 | -4903.5678 | -5491.996 | -6151.0355 | -6889.1597 | -7715.8589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Free Cash Flow |  |  |  |  | -62303.2357 | -4593.8675 | -5073.5344 | -5590.8418 | -6150.0814 | -6756.0543 | 1227.6299 | 1029.9427 | 829.6352 | 626.6469 | 420.9164 | 212.3808 | 0.97629 | -213.3624 | -430.7018 | -6756.1887 | -874.6546 | -1101.4074 | -1331.4398 | -1564.8248 | -1801.6369 | -2041.9522 | -2285.8481 | -3536.541 | -3781.8177 | -4030.9527
| Equity Cash Flow |  |  |  |  | -31151.6179 | -4593.8675 | -5073.5344 | -5590.8418 | -6150.0814 | -6756.0543 | 1227.6299 | 1029.9427 | 829.6352 | 626.6469 | 420.9164 | 212.3808 | 0.97629 | -213.3624 | -430.7018 | -6756.1887 | -874.6546 | -1101.4074 | -1331.4398 | -1564.8248 | -1801.6369 | -2041.9522 | -2285.8481 | -3536.541 | -3781.8177 | -4030.9527
Equity Payback Flag
| Cumulative Equity Cash Flow |  |  |  |  | -31151.6179 | -35745.4854 | -40819.0197 | -46409.8615 | -52559.9429 | -59315.9973 | -58088.3673 | -57058.4246 | -56228.7895 | -55602.1426 | -55181.2262 | -54968.8453 | -54967.869 | -55181.2315 | -55611.9333 | -62368.122 | -63242.7765 | -64344.1839 | -65675.6237 | -67240.4485 | -69042.0854 | -71084.0376 | -73369.8857 | -76906.4266 | -80688.2443 | -84719.197
| Balance Sheet | [7 empty] | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Assets
| Depreciation & Amortization | [5 empty] | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 2663.1642 | 1946.36 | 1946.36 | 1946.36 | 1946.36 | 1946.36 | 1946.36 | 1946.36 | 1946.36 | 1946.36 | 1946.36
| Total tangible assets (after depreciation) |  |  |  |  | 55590.7357 | 52927.5715 | 50264.4073 | 47601.243 | 44938.0788 | 42274.9146 | 39611.7504 | 36948.5861 | 34285.4219 | 31622.2577 | 28959.0934 | 26295.9292 | 23632.765 | 20969.6008 | 18306.4365 | 21748.3515 | 19801.9915 | 17855.6316 | 15909.2716 | 13962.9116 | 12016.5516 | 10070.1916 | 8123.8316 | 6177.4717 | 4231.1117 | 2284.7517
| Cash | [5 empty] | -4593.8675 | -9667.4019 | -15258.2437 | -21408.3251 | -28164.3794 | -26936.7495 | -25906.8068 | -25077.1716 | -24450.5247 | -24029.6083 | -23817.2275 | -23816.2512 | -24029.6136 | -24460.3154 | -31216.5041 | -32091.1587 | -33192.5661 | -34524.0059 | -36088.8306 | -37890.4675 | -39932.4197 | -42218.2678 | -45754.8088 | -49536.6265 | -53567.5792
| Total Assets |  |  |  |  | 55590.7357 | 48333.704 | 40597.0054 | 32342.9994 | 23529.7537 | 14110.5352 | 12675.0009 | 11041.7793 | 9208.2503 | 7171.733 | 4929.4851 | 2478.7017 | -183.4862 | -3060.0129 | -6153.8789 | -9468.1526 | -12289.1671 | -15336.9345 | -18614.7343 | -22125.919 | -25873.9159 | -29862.2281 | -34094.4362 | -39577.3371 | -45305.5148 | -51282.8275
Equity and Liabilities
| Equity + Grant - Non tangible costs |  |  |  |  | 24439.1179 | 26308.2149 | 27883.0979 | 29128.4612 | 30004.7623 | 30467.7138 | 30467.7138 | 30467.7138 | 30467.7138 | 30467.7138 | 30467.7138 | 30467.7138 | 30467.7138 | 30467.7138 | 30467.7138 | 30467.7138 | 30467.7138 | 30467.7138 | 30467.7138 | 30467.7138 | 30467.7138 | 30467.7138 | 30467.7138 | 30467.7138 | 30467.7138 | 30467.7138
| Retained earnings previous years | [6 empty] | -4222.561 | -8042.1466 | -11390.4804 | -14190.8675 | -16357.1786 | -17792.713 | -19425.9345 | -21259.4636 | -23295.9809 | -25538.2287 | -27989.0121 | -30651.2 | -33527.7267 | -36621.5927 | -39935.8664 | -42756.8809 | -45804.6484 | -49082.4481 | -52593.6329 | -56341.6297 | -56341.6297 | -56341.6297 | -56341.6297 | -56341.6297
| Retained earnings actual year | [5 empty] | -4222.561 | -3819.5856 | -3348.3338 | -2800.387 | -2166.3112 | -1435.5343 | -1633.2215 | -1833.5291 | -2036.5173 | -2242.2478 | -2450.7834 | -2662.1879 | -2876.5267 | -3093.866 | -3314.2737 | -2821.0146 | -3047.7674 | -3277.7998 | -3511.1847 | -3747.9969 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12
| Bridge Finance Long term liabilities |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Standard Project Debt Long term liabilities |  |  |  |  | 31151.6179 | 26248.05 | 20756.0541 | 14605.0186 | 7715.8589 | 0 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -4.5475e-12 | -3988.3122 | -4232.2081 | -5482.901 | -5728.1777 | -5977.3127
| Total Equity and Liabilities |  |  |  |  | 55590.7357 | 48333.704 | 40597.0054 | 32342.9994 | 23529.7537 | 14110.5352 | 12675.0009 | 11041.7793 | 9208.2503 | 7171.733 | 4929.4851 | 2478.7017 | -183.4862 | -3060.0129 | -6153.8789 | -9468.1526 | -12289.1671 | -15336.9345 | -18614.7343 | -22125.919 | -25873.9159 | -29862.2281 | -30106.124 | -31356.8169 | -31602.0936 | -31851.2286
| KEY PERFORMANCE METRICS | [7 empty] | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Levelized Cost of Electricity
| LCOE without Grant | [5 empty] | 0.099048 |  | 4: 1496821.0061
| LCOE with Grant | [5 empty] | 0.099048
Debt Service
| Cash Available for Debt Service | [5 empty] | 2178.7974 | 1993.3446 | 1805.5569 | 1615.3794 | 1422.7561 | 1227.6299 | 1029.9427 | 829.6352 | 626.6469 | 420.9164 | 212.3808 | 0.97629 | -213.3624 | -430.7018 | -651.1095 | -874.6546 | -1101.4074 | -1331.4398 | -1564.8248 | -1801.6369 | -2041.9522 | -2285.8481 | -3536.541 | -3781.8177 | -4030.9527
| Total Debt Service | [5 empty] | 8641.762 | 8641.762 | 8641.762 | 8641.762 | 8641.762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Debt Service Coverage Ratio | [5 empty] | 0.25212 | 0.23066 | 0.20893 | 0.18693 | 0.16464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Min Debt Service Coverage Ratio | [5 empty] | 0.25212 | 0.23066 | 0.20893 | 0.18693 | 0.16464 | 0.16464 | 0.16464 | 0.16464 | 0.16464 | 0.16464 | 0.16464 | 0.16464 | 0.16464 | 0.16464 | 0.16464 | 0.16464 | 0.16464 | 0.16464 | 0.16464 | 0.16464 | 0.16464 | 0.16464 | 0.16464 | 0.16464 | 0.16464
Profit Margin
| Operating Profit Margin | [5 empty] | -5.499% | -7.65% | -9.854% | -12.11% | -14.42% | -16.79% | -19.22% | -21.71% | -24.26% | -26.87% | -29.55% | -32.29% | -35.1% | -37.98% | -40.93% | -35.05% | -38.1% | -41.22% | -44.42%
| Average Operating Profit Margin | [5 empty] | -5.499% | -6.574% | -7.667% | -8.778% | -9.908% | -11.06% | -12.22% | -13.41% | -14.61% | -15.84% | -17.09% | -18.35% | -19.64% | -20.95% | -22.28% | -23.08% | -23.96% | -24.92% | -25.95% | -25.95% | -25.95% | -25.95% | -25.95% | -25.95% | -25.95%
| Minimum Operating Profit Margin | [5 empty] | -5.499% | -7.65% | -9.854% | -12.11% | -14.42% | -16.79% | -19.22% | -21.71% | -24.26% | -26.87% | -29.55% | -32.29% | -35.1% | -37.98% | -40.93% | -40.93% | -40.93% | -41.22% | -44.42% | -44.42% | -44.42% | -44.42% | -44.42% | -44.42% | -44.42%
Net Present Value
| Project NPV | [5 empty] | -18370.2599 | -24837.0595 | -30294.1416 | -34799.2378 | -38404.8222 | -41158.4983 | -43708.4411 | -46071.1396 | -48261.6832 | -50293.8825 | -52180.3795 | -53932.7484 | -55561.5879 | -57076.6049 | -58629.2531 | -59880.8295 | -61062.0147 | -62177.1905 | -63230.4318 | -64225.5304 | -65166.0168 | -66055.1803 | -67066.9368 | -68019.6921 | -68917.199
| Equity NPV | [5 empty] | -12716.768 | -19804.1833 | -26698.96 | -33421.5701 | -39991.4942 | -40981.5248 | -41956.0153 | -42913.2515 | -43851.7836 | -44770.4004 | -45668.1056 | -46544.0963 | -47397.7424 | -48228.5695 | -50069.8099 | -50823.2497 | -51562.6805 | -52286.8641 | -52994.7791 | -53685.5974 | -54358.6634 | -55013.4752 | -55820.5169 | -56595.0896 | -57338.1387
Internal Rate of Return
| Project IRR | [5 empty] | -9.074% | -8.393% | -7.928% | -7.51% | -7.071% | -6.577% | -6.297% | -6.169% | -6.158% | -6.246% | -6.424% | -6.695% | -7.067% | -7.561% | -8.037% | -8.399% | -8.904% | -9.594% | -10.55% | -11.92% | -14.02% | N/A | N/A | N/A | N/A
| Equity IRR | [5 empty] | 23.18% | 8.149% | 0.7651% | -3.949% | -7.5% | -6.763% | -6.378% | -6.209% | -6.191% | -6.292% | -6.497% | -6.805% | -7.224% | -7.775% | -8.292% | -8.672% | -9.206% | -9.935% | -10.93% | -12.35% | -14.49% | N/A | N/A | N/A | N/A
| Project life | 25 | years
| LCOE without Grant | 0.099048 | $/kWh
| LCOE with Grant | 0.099048 | $/kWh
| Minimum DSCR | Less than 1 | ratio
| Project NPV | -68917.199 | USD
| Equity NPV | -57338.1387 | USD
| Project IRR | 0% | %
| Equity IRR | 0% | %
| Equity Payback period | 0 | years
| Return on Investment | -29.12% | %
| Discounted ROI | -4.252% | %
Note on C279: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Is project development cost also to be depreciated?

## Backend Values
Backend Values
Diff. from estimate | Inverter Sizes |  |  | Difference from Estimate | Size of the Cable (Sq. mm)
NA | 3 | kW |  | NA | 2.5
NA | 4 | kW |  | NA | 4
NA | 5 | kW |  | 1 | 6
NA | 7.5 | kW |  | 5 | 10
NA | 9 | kW |  | 11 | 16
NA | 15 | kW |  | 20 | 25
NA | 20 | kW |  | 30 | 35
NA | 25 | kW |  | 45 | 50
25 | 25 | kW |  | 65 | 70
25 |  |  |  | 90 | 95
|  |  |  | 115 | 120
Diff. from estimate | MCB/MCCB Size |  |  | 145 | 150
NA | 6 | Ampere |  | 1
NA | 10 | Ampere
NA | 16 | Ampere
NA | 32 | Ampere
5.5 | 63 | Ampere
42.5 | 100 | Ampere
42.5 | 100 | Ampere
5.5
AC Wire Sizing Chart
Adopted Wire Sizing Formulae
Wire Size in circular mills = (d*2*I*k)/(V*Vd)
where,
· d = 1-way wire distance
· I = Maximum continuous current rating of the inverter
· V = Nominal utility voltage (i.e. 240, 208 etc.)
· V_d = Percentage voltage drop, for 1% , 0.01
· k = thermal conductivity of the "K- Factor" of a metal; for Copper use 12.9
Approximate Wire Sizing
S.no. | AC Wire Description | Length in meter | Allowable % Voltage drop | Voltage System (V) | Max current in Ampere | Wire Size in circular mills | Area mm2 (equivalent) | Available nearest Size wire (mm2) / phase
1 | Inverter to AC Combiner Box | 40 | 2 | 400 | 71.875 | 9271.875 | 5 | 6
[7 empty] | CM | MM2
[7 empty] | 1 | 0.00050671
Note on B16: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Review once again-NR
Note on D40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Distance taken as 10 meters for each inverter

## Reference Prices
Reference Prices
Components ¦ Users may update prices if required
MCB-TPN/MCCB 25kA |  |  |  | Lightning Arrestor |  |  |  |  | Others
Size | Price | Remarks |  | Type | Price | Remarks |  |  | Item | Unit | Cost
6 | 1710 | Kathmandu District Rate 77/78 |  | ESE Type | 85000 | Standard Average Pricing |  |  | Solar Panel | kWp | 35000
10 | 1710 | Kathmandu District Rate 77/78 |  | Copper Spike | 5500 | Standard Average Pricing |  |  | Alumunum angle/GI truss | kWp | 9000
16 | 1710 | Kathmandu District Rate 77/78 |  | Copper Strip (25 x 3) / Kg | 1082 | Kathmandu District Rate 77/78 |  |  | Remote Monitoring unit | Pcs. | 65000
32 | 6386 | Kathmandu District Rate 77/78 | [6 empty] | Energy meter | Pcs. | 31000
63 | 6386 | Kathmandu District Rate 77/78 | [6 empty] | DC Cable (PV Strings) | meters | 105
100 | 7045 | Kathmandu District Rate 77/78 | [6 empty] | DC MCB-String | Pcs. | 3578
63 | [8 empty] | PV Combiner Box | Pcs. | 10700
[9 empty] | Earthing rod | Pcs. | 10000
DC Cables, 2C, Unarmoured |  |  |  | AC Cables, 4C, Unarmoured |  |  |  |  | Inverters
Size | Price | Remarks |  | Size | Price | Remarks |  |  | Size |  | Price
2.5 | 103 | Kathmandu District Rate 77/78 |  | 2.5 | 170 | Kathmandu District Rate 77/78 |  |  | 3 |  | 280000
4 | 144 | Kathmandu District Rate 77/78 |  | 4 | 252 | Kathmandu District Rate 77/78 |  |  | 4 |  | 320000
6 | 196 | Kathmandu District Rate 77/78 |  | 6 | 350 | Kathmandu District Rate 77/78 |  |  | 5 |  | 355000
10 | 309 | Kathmandu District Rate 77/78 |  | 10 | 556 | Kathmandu District Rate 77/78 |  |  | 7.5 |  | 390000
16 | 427 | Kathmandu District Rate 77/78 |  | 16 | 845 | Kathmandu District Rate 77/78 |  |  | 9 |  | 420000
25 | 659 | Kathmandu District Rate 77/78 |  | 25 | 1318 | Kathmandu District Rate 77/78 |  |  | 12 |  | 490000
35 | 896 | Kathmandu District Rate 77/78 |  | 35 | 1772 | Kathmandu District Rate 77/78 |  |  | 15 |  | 510000
50 | 1236 | Kathmandu District Rate 77/78 |  | 50 | 2472 | Kathmandu District Rate 77/78 |  |  | 20 |  | 560000
70 | 1236 | Kathmandu District Rate 77/78 |  | 70 | 3451 | Kathmandu District Rate 77/78 |  |  | 25 |  | 590000
95 | 2318 | Kathmandu District Rate 77/78 |  | 95 | 4687 | Kathmandu District Rate 77/78 |  |  | 25
120 | 3039 | Kathmandu District Rate 77/78 |  | 120 | 5923 | Kathmandu District Rate 77/78
150 | 3811 | Kathmandu District Rate 77/78 |  | 150 | 7365 | Kathmandu District Rate 77/78
4 |  |  |  | 185 | 9064 | Kathmandu District Rate 77/78
|  |  |  | 240 | 12257 | Kathmandu District Rate 77/78
|  |  |  | 300 | 14832 | Kathmandu District Rate 77/78
|  |  |  | 400 | 20085 | Kathmandu District Rate 77/78
6
Components of Bill of Quantities (BoQ)
[6 empty] | NPR/Wp | 65
SN | Component |  | Specification | Qty | Units | Unit Cost (NPR) | Non-Vatable amount (NPR) | Vatable amount (NPR) | Remarks
1 | Solar Panel |  | Monocrystalline | 101 | kWp | 35000 | 3535000 |  | Rs. 35/Watt
2 | Aluminum Angle |  | 2x2 Aluminum Frame and relevant Accessories | 101 | kWp | 9000 |  | 909000 | Rs.9/Watt
3 | Grid Connected Inverter |  | 25 kW | 4 | Pcs. | 590000 | 2360000 |  | Price Reference-SMA
4 | Remote Monitoring Unit |  | As per the selected inverter | 1 | Pcs. | 65000 |  | 65000 | Standard Average Pricing
5 | Energy Meter |  | NEA Standard | 0 | Pcs. | 31000 |  | 0 | Standard Average Pricing
6 | DC Cable (PV Strings) |  | 4Sq.mm, 1100V, 1 Core | 309 | Meters | 105 |  | 32445 | Kathmandu District Rate 77/78; Size: Assuming Max. 50 meters distance for a single string and 16 modules/string; Per module cable length=1.5mtrs
7 | DC Cable(From Array to Power House) |  | 4 Sq.mm | 50 | Meters | 144 |  | 7200 | Kathmandu District Rate 77/78
8 | AC Cable from String Inverters to AC Combiner Box |  | 6 Sq.mm, 4 Core, Unarmoured | 40 | Meters | 350 |  | 14000
9 | DC MCB-String |  | 20A/1000V | 13 | Pcs. | 3578 |  | 46514 | Standard Average Pricing
10 | AC MCB/MCCB-25kA |  | 63 Amp | 5 | Pcs. | 6386 |  | 31930 | Kathmandu District Rate 77/78
11 | PV Combiner Box |  | IP66 with in-built SPD | 2 | Pcs. | 10700 |  | 21400 | Standard Average Pricing
12 | Lightning Arrestor |  | ESE Type | 1 | Pcs. | 85000 |  | 85000 | Standard Average Pricing
13 | Earthing rod |  | Chemical Earthing | 4 | Pcs. | 10000 |  | 40000 | Standard Average Pricing
13 | Copper Strip & Insulators |  | 25 x 5, Approx, 1.5 mtr. =1kg | 27 | kg | 1082 |  | 29214 | Kathmandu District Rate 77/78
14 | Installation Accessories |  | nut bolts, cable tie, tapes, conduits, cable tray etc. | 1 | LS | 606000 |  | 606000 | Rs. 8/Wp
15 | Installation Labor & Transportation |  | Skilled, Semi-Skilled Technician, Engineer etc. | 1 | Ls | 505000 |  | 505000 | Rs. 6/Wp
16 | Contigency-5% |  | 5% of the total cost | 1 |  |  | 294750 | 119635.15
[6 empty] | Sub-Total | 6189750 | 2512338.15 | NPR
[7 empty] | VAT(13%) | 326603.9595 | NPR
Note: This is BoQ is indicative only. The final BoQ requires Detailed Feasibility Study to be completed. | [6 empty] | Grand Total | 6516353.9595 | NPR
Note on E49: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Assuming all the modules are connected in series for a string
Note on E54: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Designer may choose any other value depending upon the requirement. This is the standard value used.